## Instructions
Readily Available Permit: Engine Power Generation (RAP: PowerEngine)
Air Permits Division
Texas Commission on Environmental Quality
TCEQ 20952, Version 2.1
This sheet is for informational purposes only. No data is required and you do not need to print this sheet. This sheet provides guidance on the RAP: PowerEngine criteria and instructions for preparing and submitting an application.
I. Overview
The RAP: PowerEngine is a case-by-case New Source Review (NSR) project to authorize operation of up to ten diesel-fired engines and up to ten associated diesel storage tanks for the purpose of power generation. This RAP authorization is only applicable for a new permit. This RAP: PowerEngine application workbook provides administrative and technical information needed by the Texas Commission on Environmental Quality (TCEQ) to evaluate operation of the engine(s) and associated equipment. The qualification criteria for this RAP is contained within this workbook and must be agreed to by the applicant at the time of submittal of the RAP application. Facilities shall be constructed and operated as specified in the permit application. All representations regarding construction plans and operation requirements contained in the permit application (including this workbook) shall be enforceable representations upon issuance of the project. Accessibility disclaimer: this workbook contains intentionally blank cells.
II. Qualification Criteria
The following qualification criteria must be met in order to submit an application for the RAP: PowerEngine.
1. The project is for up to ten diesel-fired engines and up to ten associated diesel storage tanks.
2. The engines are limited to a combined total of 300 hours of operation per rolling 12-month period. This limit applies collectively to all engines at the site which are authorized by a RAP: PowerEngine.
3. Maximum emission rates are listed on the engine and tank sheets of this workbook. These maximums represent the combined maximum for all engines at the site authorized by a RAP and all diesel tanks at the site authorized by a RAP.
4. Project emission increases represented in this RAP will not exceed the PSD or Nonattainment NSR major source thresholds at existing minor sites or netting thresholds at existing major sites. Emission decreases are not to be included when determining project emission increases.
5. There are no upstream or downstream production increases as a result of this project. There is no increase to actual emission rates for sources outside of this current RAP workbook. See Title 30 Texas Administrative Code (TAC) Chapter 116 for additional information.
6. General sitewide MSS activities not associated with the engines authorized in this RAP are not included in this project and are not authorized by this RAP.
7. The customer has a compliance history classification of Satisfactory or High (further information on compliance history classifications and details on obtaining a compliance history report can be found at the links listed at the end of this sheet).
8. The facility will comply with all of the following, as listed in this workbook: • Emission sources and rates; • Best Available Control Technology (BACT); • The Air Quality Analysis; • Special Conditions; and • Representations made in this application workbook.
III. Process Instructions
1. Prepare all items to make the complete application. Follow "Section IV. Workbook Instructions" below to complete the application workbook. A complete application for this RAP includes the following: • Process flow diagram • Current area map • Plot plan • RAP: PowerEngine Application Workbook (The file name should be: Date_ApplicationWorkbook_Company name_Permit number) • Engine supporting documentation and stack test data • If the project involves diesel tank(s): storage tank emission calculations or output files from approved calculation software • If using baseline emissions in the federal applicability determination, attach a printout from Emissions Inventory showing the baseline emission years for the units in the project. 2. Submit the application through STEERS as an ePermits application. When submitting through STEERS a wet signature is not required and the system will notify the appropriate regional office and local program(s). You are still required to provide a hard copy of the application to be displayed at the public viewing location during public notice. 3. Submit all application attachments through STEERS as part of your ePermit application unless: • the file size of an attachment exceeds 50 MB or • the file type is not accepted (accepted file types are xls, xlsm, xlsx, txt, pdf, doc, docx, wpd, csv, xml, jpg, gif, tif, and jpeg). If the attachment cannot be submitted through STEERS for one of the reasons listed above, submit the attachment through email or TCEQ FTPS. For the initial submittal, you must share these files with APIRT@tceq.texas.gov. Once your project is assigned, you will share files directly with your reviewer. If confidential files will be submitted, follow the additional instructions below. Confidential files must be submitted through STEERS or the TCEQ FTPS. All pages must be marked confidential and have confidential in the file name. Confidential submittals must be separate from non-confidential application materials. Note: emails sent to the agency are not encryption protected via Secure Sockets Layers by our server and may be subject to interception by common third-party internet tools. Anything marked as confidential will be treated as such by APD staff upon receipt.
4. Submit copies of the application materials to other applicable program areas in accordance with "Section VI. Where to Submit Application Materials" below. 5. Do not begin construction until notified by the TCEQ. 6. If the qualification criteria are not met, or if the applicant does not agree with the RAP-SCT Special Conditions, the applicant will receive notice that the application has been voided and the applicant should seek a different type of authorization as appropriate. See the below link for additional information about submitting via FTPS:
https://ftps.tceq.texas.gov/help/
IV. Workbook Instructions
1. Complete the workbook sheets in order, moving left to right and top to bottom. 2. Complete all input cells on each applicable emission source sheet. • Enter the emission point number (EPN) and facility identification number (FIN). • Some cells have drop-down selections. 3. On the "CND" sheet, confirm acceptance of all information in this workbook and submitted with the application. 4. Under Texas Government Code 559.003(a), Individuals are entitled to receive and review any information collected by TCEQ about the individual by means of a form that that is completed and filed with TCEQ in a paper or electronic format on the TCEQ website consistent with Texas Government Code sec., 559.003(b). The individual is also entitled to have TCEQ correct information about the individual that is incorrect. If you have questions on how to fill out this form or about the air permits program, please contact us at 512-239-1250.
V. Website Links:
Combustion BACT | https://www.tceq.texas.gov/permitting/air/nav/air_bact_combustsources.html
STEERS | https://www3.tceq.texas.gov/steers/
FTPS Information | https://ftps.tceq.texas.gov/help/
Core Data Form | www.tceq.texas.gov/permitting/central_registry/guidance.html
Compliance history classifications | www.tceq.texas.gov/compliance/enforcement/compliance-history/about.html
Compliance history report | www.tceq.texas.gov/compliance/enforcement/compliance-history/get_report.html
Local Air Pollution Control Programs | www.tceq.texas.gov/permitting/air/local_programs.html
Texas Government Code 559 | https://statutes.capitol.texas.gov/Docs/GV/htm/GV.559.htm#559.003
TCEQ Regional Offices | www.tceq.texas.gov/agency/directory/region
VI. Where to Submit Application Materials
Who | Where | When | What
Air Permits Division Air Permits Initial Review Team (APIRT) | STEERS (link above) | All applications | Application workbook (this file) and application attachments.
Financial Administrative Division Revenue Operations Section | Regular, Certified, Priority Mail MC 214, P.O. Box 13088, Austin, Texas 78711-3088 or Hand Delivery, Overnight Mail Mail Code 214, 12100 Park 35 Circle, Building A, Third Floor, Austin, Texas 78753 Note: The official application cannot be faxed | All applications not using ePay | Fee, copy of the PI-1-PowerEngine sheet, and Core Data Form (link above)
Alabama-Coushatta Tribe of Texas | 571 State Park Road 56, Livingston, Texas 77351 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the PI-1-PowerEngine sheet, all attachments, public notice, and affidavit
Kickapoo Traditional Tribe of Texas | Box HC 1, 9700, Eagle Pass, Texas 78852 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the PI-1-PowerEngine sheet, all attachments, public notice, and affidavit
Ysleta del Sur Pueblo of Texas | 119 S. Old Pueblo Rd., El Paso, Texas 79907 | If the proposed facilities are located within 100 km or less of the Indian Tribal Lands | Copies of the PI-1-PowerEngine sheet, all attachments, public notice, and affidavit
EMD Division Chief International Boundary and Water Commission United States Section | 4171 N. Mesa, Suite C-100, El Paso, Texas 79902-1441 | If new construction is proposed within 100 km of the Rio Grande River | Copies of the PI-1-PowerEngine sheet and all attachments
VII. Workbook Table of Contents (click to jump to the sheet)
Instructions
General application materials
PI-1-PowerEngine: General Application for RAP: PowerEngine
Estimated Capital Cost and Fee Verification
Specific source information (sheets not needed for this project will be greyed out)
Engine 1
Engine 2
Engine 3
Engine 4
Engine 5
Engine 6
Engine 7
Engine 8
Engine 9
Engine 10
Engine Summary
Tanks
Additional application materials
Public Notice Applicability and Small Business Classification
Baseline Emission Information
Federal Applicability Determination
Best Available Control Technology (BACT)
Air Quality Analysis (AQA)
Toxicology Review (Tox)
Special Conditions and Agreement (CND)
Project Summary
End of sheet. Click here to move to the next sheet.
End of sheet. Click here to move to the next sheet.

## PI-1-PowerEngine
PI-1-PowerEngine |  | Applicant Internal Comments | GRAY CF | RED CF
This sheet provides administrative and technical information needed by the TCEQ and is required for a RAP: PowerEngine application. Instructions: 1. Complete all sections below. |  | All comments must be deleted prior to application submittal.
I. Applicant Information
I acknowledge that I am submitting an authorized TCEQ application workbook and any necessary attachments. Except for inputting the requested data and adjusting row height, I have not changed the TCEQ application workbook in any way, including but not limited to changing formulas, formatting, content, or protections. |  |  |  | FALSE
A. Company Information
Company or Legal Name:
Permits are issued to either the facility owner or operator, commonly referred to as the applicant or permit holder. List the legal name of the company, corporation, partnership, or person who is applying for the permit. We will verify the legal name with the Texas Secretary of State at (512) 463-5555 or at the link below:
www.sos.state.tx.us
Texas Secretary of State Charter/Registration Number (if given):
B. Company Official Contact Information: must not be a consultant
Requested Information | Response
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
C. Technical Contact Information: This person must have the authority to make binding agreements and representations on behalf of the applicant and may be a consultant.
Requested Information | Response
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Company or Legal Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
D. Assigned Numbers
Requested Information | Response
Customer Number (CN): The CN is a unique number given to each business, governmental body, association, individual, or other entity that owns, operates, is responsible for, or is affiliated with a regulated entity. If not yet assigned, leave blank.
Regulated Entity Reference Number (RN): The RN is a unique agency assigned number given to each person, organization, place, or thing that is of environmental interest to us and where regulated activities will occur. The RN replaces existing air account numbers. The RN is also assigned if the agency has conducted an investigation or if the agency has issued an enforcement action. If not yet assigned, leave blank.
Is this facility located at a site required to obtain a federal operating permit (FOP)?
If Yes, list all associated FOP number(s). If no associated permit number has been assigned yet, enter "TBD." |  |  | FALSE
II. Facility Location and General Information
A. Location
Requested Information | Response
County: Enter the county where the facility will be physically located.
Street Address:
City: If the address is not located in a city, then enter the city or town closest to the facility, even if it is not in the same county as the facility.
ZIP Code: Include the ZIP Code of the physical facility site, not the ZIP Code of the applicant's mailing address.
Site Location Description: If there is no street address, provide written driving directions to the site. Identify the location by distance and direction from well-known landmarks such as major highway intersections.
B. General Information
Site Name:
Area Name: Must indicate the general type of operation, process, equipment or facility. Include numerical designations, if appropriate. Examples are Sulfuric Acid Plant and No. 5 Steam Boiler. Vague names such as Chemical Plant are not acceptable.
Are there any schools located within 3,000 feet of the site boundary?
C. Industry Type
Principal Company Product/Business:
A list of SIC codes can be found at the link below:
www.osha.gov/pls/imis/sicsearch.html
Principal SIC code:
NAICS codes and conversions between NAICS and SIC Codes are available at the link below:
https://www.census.gov/naics/
Principal NAICS code:
D. State Senator and Representative for this site
This information can be found at the link below:
https://wrm.capitol.texas.gov/home
State Senator:
District:
State Representative:
District:
III. Project Information
A. Description
Is this an application for a new minor permit? | Yes
How many engines are included in this application?
How many diesel tanks are included in this application?
Revise the provided process description to represent your project and site specifics. (Limited to 5000 characters.)
B. Project Timing You must obtain an air authorization before beginning construction. Construction is broadly interpreted as anything other than site clearance or site preparation. Enter the date as "Month Date, Year" (e.g. July 4, 1776).
Projected Start of Construction:
Projected Start of Operation:
C. Enforcement Projects
Is this application in response to, or related to, an agency investigation, notice of violation, or enforcement action?
If yes, did you attach copies of any correspondence from the agency and provide the RN associated with the investigation, notice of violation, or enforcement action? |  |  | FALSE
D. Operating Schedule
Provide details about the engine(s) operating schedule. Note: The engines are limited to a combined total of 300 hours of operation per rolling 12 month permit. This limit applies collectively to all engines at the site which are authorized by any RAP: PowerEngine permit action.
IV. State Regulatory Questions
Indicate if any of the following requirements apply to the proposed facility and demonstrate that the proposed facility can, or is, complying with the applicable requirements. Briefly (500 characters or fewer) demonstrate how compliance with each of the applicable requirements can be met. Additional pages may be attached, if necessary.
A. 30 TAC Chapter 101 - General Air Rules
Will the facility protect public health/welfare and comply with all rules/regulations of the TCEQ? |  |  |  | FALSE
How will this facility comply with the requirements of this chapter?
B. 30 TAC Chapter 111 - Visible Emissions and Particulate Matter
Does 30 TAC Chapter 111 apply to this facility?
If applicable, how will this facility comply with the requirements of this chapter? |  |  | FALSE
C. 30 TAC Chapter 112 - Sulfur Compounds
Does 30 TAC Chapter 112 apply to this facility?
If applicable, how will this facility comply with the requirements of this chapter? |  |  | FALSE
D. 30 TAC Chapter 113 - Toxic Materials
Does 30 TAC Chapter 113 apply to this facility?
If applicable, how will this facility comply with the requirements of this chapter? |  |  | FALSE
E. 30 TAC Chapter 115 - Volatile Organic Compounds
Does 30 TAC Chapter 115 apply to this facility?
If applicable, how will this facility comply with the requirements of this chapter? |  |  | FALSE
F. 30 TAC Chapter 117 - Nitrogen Compounds
Does 30 TAC Chapter 117 apply to this facility?
If applicable, how will this facility comply with the requirements of this chapter? |  |  | FALSE
V. Required Attachments
A. Confidential Application Materials
Is confidential information submitted with this application?
If yes, is each confidential page marked "CONFIDENTIAL" in large red letters? |  |  | FALSE | FALSE
THSC §382.041 restricts whether confidential information can be disclosed. Mark any information related to secret or proprietary processes or methods of manufacture as confidential if you do not want this information in the public file. All confidential information should be separated from the application and submitted as a separate file. Additional information regarding confidential information can be found at the link below: |  |  | FALSE
www.tceq.texas.gov/permitting/air/confidential.html |  |  | FALSE
B. Is a current area map attached? |  |  |  | FALSE
Is the area map current with a true north arrow, an accurate scale, the entire plant property, the location of the property relative to prominent geographical features including, but not limited to, highways, roads, streams, and significant landmarks such as buildings, residences, schools, parks, hospitals, day care centers, and churches? |  |  |  | FALSE
Does the map show a 3,000-foot radius from the property boundary? |  |  |  | FALSE
C. Is a plot plan attached? |  |  |  | FALSE
Does your plot plan clearly show a north arrow, an accurate scale, all property lines, all emission points, buildings, tanks, process vessels, other process equipment, and two bench mark locations? |  |  |  | FALSE
Does your plot plan identify all emission points on the affected property, including all emission points authorized by other air authorizations, construction permits, PBRs, special permits, and standard permits? |  |  |  | FALSE
Did you include a table of emission points indicating the authorization type and authorization identifier, such as a permit number, registration number, or rule citation under which each emission point is currently authorized? |  |  |  | FALSE
D. Is a process flow diagram attached? |  |  |  | FALSE
Is the process flow diagram sufficiently descriptive so the permit reviewer can determine the raw materials to be used in the process; all major processing steps and major equipment items; individual emission points associated with each process step; the location and identification of all emission abatement devices; and the location and identification of all waste streams (including wastewater streams that may have associated air emissions)? |  |  |  | FALSE
E. Is a Public Involvement Plan (PIP) reqiured for this project?
Is the PIP Form (TCEQ Form 20960) attached?
Requirements can be found at the following link: | https://www.tceq.texas.gov/permitting/air#pip
VI. Delinquent Fees and Penalties
Does the applicant have unpaid delinquent fees and/or penalties owed to the TCEQ? |  |  |  |  | FALSE
This form will not be processed until all delinquent fees and/or penalties owed to the TCEQ or the Office of the Attorney General on behalf of the TCEQ is paid in accordance with the Delinquent Fee and Penalty Protocol. For more information regarding Delinquent Fees and Penalties, go to the TCEQ Web site at the link below:
www.tceq.texas.gov/agency/financial/fees/delin
End of sheet. Click here to move to the next sheet.

## Fees
Estimated Capital Cost and Fee Verification |  | Applicant Internal Comments
This sheet determines application fee requirements for projects which require a fee. Fees are due and payable at the time an application is filed. Required fees must be received before the agency will consider an application to be complete. Applications will not be considered for review nor will any time constraints required of TCEQ for application processing begin until a fee is received. (30 TAC § 116.143) All permit review fees shall be remitted by check, certified check, electronic funds transfer, or money order payable to the Texas Commission on Environmental Quality (TCEQ) and mailed to the TCEQ, P.O. Box 13088, MC 214, Austin, Texas 78711-3088. The State Treasury will not accept checks drawn on foreign banks. Instructions for online payment through the ePay system can be found at the link below: |  | All comments must be deleted prior to application submittal.
https://www3.tceq.texas.gov/epay/
Instructions: 1. Answer each of the questions in Section I. 2. Enter the amount of each cost in the associated box. Include estimated cost of equipment and services that would normally be capitalized according to standard and generally accepted corporate financing and accounting procedures. 3. Enter payment information. 4. If applicable, submit the application under the seal of a Texas Licensed P.E.
I. General Information
Requested Information | Response
A fee of $75,000 shall be required if no estimate of capital project cost is included with the permit application. (30 TAC § 116.141(d)) Select "yes" here to use this option. Then skip sections II and III.
Select Application Type
II. Direct Costs
Type of Cost | Amount
Process and control equipment not previously owned by the applicant and not currently authorized under this chapter.
Auxiliary equipment, including exhaust hoods, ducting, fans, pumps, piping, conveyors, stacks, storage tanks, waste disposal facilities, and air pollution control equipment specifically needed to meet permit and regulation requirements.
Freight charges.
Site preparation, including demolition, construction of fences, outdoor lighting, road, and parking areas.
Installation, including foundations, erection of supporting structures, enclosures or weather protection, insulation and painting, utilities and connections, process integration, and process control equipment.
Auxiliary buildings, including materials storage, employee facilities, and changes to existing structures.
Ambient air monitoring network.
Sub-Total: | 0
III. Indirect Costs
Type of Cost | Amount
Final engineering design and supervision, and administrative overhead.
Construction expense, including construction liaison, securing local building permits, insurance, temporary construction facilities, and construction clean-up.
Contractor's fee and overhead.
Sub-Total: | 0
IV. Calculations
In signing the application during STEERS submittal, I certify that the total estimated capital cost of the project as defined in 30 TAC §116.141 is equal to or less than the above figure. I further state that I have read and understand Texas Water Code § 7.179, which defines Criminal Offenses for certain violations, including intentionally or knowingly making, or causing to be made, false material statements or representations.
Estimated Capital Cost | Minor Application Fee
Less than $300,000 | $900 (minimum fee)
$300,000 - $25,000,000 | 0.30% of capital cost
Greater than $25,000,000 | $75,000 (maximum fee)
Your estimated capital cost: | 0
Permit Application Fee: | 0
If a fee exemption or reduction applies, describe how this facility qualifies for an exemption or reduction. Include the actual fee amount.
V. Payment Information
Requested Information | Response
Was the fee paid online?
Enter the fee amount:
Enter the check, money order, ePay Voucher, or other transaction number:
Enter the Company name as it appears on the check:
VI. Professional Engineer Seal Requirement
Requested Information | Response
Is the estimated capital cost of the project above $2 million?
Is this project subject to an exemption contained in the Texas Engineering Practice Act (TEPA)? (30 TAC § 116.110(f))
Is the application required to be submitted under the seal of a Texas licensed P.E.? Note: an electronic PE seal is acceptable.
End of sheet. Click here to move to the next sheet.

## ENGINE1
Engine 1 |  |  |  |  | Applicant Internal Comments
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE2
Engine 2 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE3
Engine 3 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE4
Engine 4 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE5
Engine 5 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE6
Engine 6 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE7
Engine 7 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1,000,000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE8
Engine 8 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE9
Engine 9 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE10
Engine 10 |  |  |  |  | Applicant Internal Comments | TRUE
This sheet details engine specifications and calculates emission rates. Instructions: 1. Complete all information below. |  |  |  |  | All comments must be deleted prior to application submittal.
I. General Information
Requested Information | Response
FIN
Source Name
UTM Zone
UTM Coordinate - Easting (meters)
UTM Coordinate - Northing (meters)
II. Input Parameters and Factors
Parameter | Value | Minimum | Maximum
Release height (ft) |  | 25 | -
Diameter (ft) |  | 0.66 | -
Temperature (°F) |  | 828 | -
Velocity (fps) |  | 168.7 | -
Rated brake power of this engine (hp) |  | - | -
Fuel consumption rate (gal diesel/hp-hr) |  | - | -
Diesel sulfur content (ppmw) |  | - | 15
Is there a selective catalytic reduction (SCR) system for this engine? |  | - | -
Is there an oxidation catalyst? |  | - | -
Is there a diesel filter? |  | - | -
Ammonia exhaust concentration (ppm) |  | - | 10 |  |  | FALSE
Annual operating schedule (hr/yr) |  | - | 300
Exhaust gas flow rate (scf/min at 60⁰F) | 0 | - | -
III. Emission Factors
Pollutant | Emission Factor | EF Unit | Source of Emission Factor | Limitations and Other Notes
NOx |  | g/hp-hr
CO |  | g/hp-hr
PM |  | g/hp-hr
PM10 |  | g/hp-hr
PM2.5 |  | g/hp-hr
VOC |  | g/hp-hr
SO2 | - | - | Material Balance | SO2 emissions determined by mass balance and assume 100% conversion of sulfur
H2SO4 | - | - | Material Balance | H2SO4 emissions determined by mass balance and assume 10% conversion of sulfur
NH3 | - | - | Material Balance | NH3 emissions calculated using ammonia concentration and exhaust flow rate |  | FALSE
IV. Emission Rates
The cells under columns “lb/hr” and “tpy” will populate automatically based upon the input parameters and emission factors entered above. Maximum emission rates are listed and are based on impacts requirements. Acceptance of the proposed emission rates for this unit is confirmed on the Special Conditions sheet.
Pollutant | lb/hr | lb/hr max* | tpy | tpy max**
NOx | 0 | 1.85 | 0 | 0.2775 |  |  | FALSE | FALSE
CO | 0 | 5.43 | 0 | - |  |  | FALSE
PM | 0 | - | 0 | -
PM10 | 0 | 0.022 | 0 | - |  |  | FALSE
PM2.5 | 0 | 0.022 | 0 | 0.0034 |  |  | FALSE | FALSE
VOC | 0 | - | 0 | -
SO2 | 0 | 0.059 | 0 | 0.0088 |  |  | FALSE | FALSE
H2SO4 | 0 | 0.0057 | 0 | - |  |  | FALSE
NH3 | 0 | 0.129 | 0 | 0.0193 |  | FALSE | FALSE | FALSE
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85. **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
V. Equations
The following equations are used to determine emission rates for each pollutant. No input is required.
A. NOx, CO, PM/PM10/PM2.5, VOC lb/hr (sample equation for NOx)
(0 hp × g/hp-hr) ÷ 453.6 lb/g = 0.00 lb/hr
B. SO2 lb/hr
(0 gal diesel/hp-hr × 7.05 lb diesel/gal diesel × 0 hp) × ( lb S ÷ 1,000,000 lb diesel) × (64 lb SO2 ÷ 32 lb S) = 0.00 lb/hr
C. H2SO4 lb/hr
(0.00 lb/hr) × (1 lb mol SO2 ÷ 64.06 lb SO2) × (0.1 lb mol SO3 ÷ 1 lb mol SO2) × (1 lb mol H2SO4 ÷ 1 lb mol SO3) × (98.07 lb H2SO4 ÷ 1 lb mol H2SO4) = 0.00 lb/hr
Note: a conservative molar assumption of 10% molar concentration was used to convert SO2 to SO3 and 100% for SO3 to H2SO4.
D. Ammonia lb/hr | [5 empty] | FALSE
(0.00 ppm NH3 × 17 lb NH3/lb-mol × 0.00 scf/min × 60 min/hr) ÷ (379.00 dscf/lb-mol × 1000000) = 0.00 lb/hr | [5 empty] | FALSE
E. All pollutants, tpy (sample equation for NOx)
(0.00 lb/hr × hr/yr) ÷ 2000 lb/ton = 0.00 tpy
End of sheet. Click here to move to the next sheet.

## ENGINE Summary
Engine Summary | [10 empty] | Applicant Internal Comments | GRAY CF
This sheet summarizes and compares engine hours of operation and emission rates to RAP limits. For multiple engines, this sheet also establishes engine cap information. Note: Section I represents the engine EPN parameters. Section II compares all engine operational hours. Section III compares all engine total and maximum lb/hr emissions against the RAP limit. Section IV compares all engine maximum and total tpy emissions against the RAP limit. Total engine emission and individual maximum emissions cannot exceed the RAP limit. | [10 empty] | All comments must be deleted prior to application submittal.
I. Engine Cap Information
Requested Information | Response
EPN
Source name
UTM zone
UTM coordinate - easting (meters)
UTM coordinate - northing (meters)
Number of engines in this project: | 0
II. Hours of Operation
Sheet ID | FIN | Annual operating hours (hr/yr) | Comment
Engine 1 | 0 | 0 | Individual operational hours are within permitted limit.
Engine 2 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 2
Engine 3 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 3
Engine 4 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 4
Engine 5 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 5
Engine 6 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 6
Engine 7 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 7
Engine 8 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 8
Engine 9 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 9
Engine 10 | 0 | 0 | Individual operational hours are within permitted limit. | [8 empty] | FALSE | 10
Total operating hours |  | 0 | Total site operating hours set at or below 300 hours annually.
III. Short-Term Emission Limit (lb/hr)
Sheet ID | FIN | NOx | CO | PM | PM10 | PM2.5 | VOC | SO2 | H2SO4 | NH3
Engine 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engine 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 2
Engine 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 3
Engine 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 4
Engine 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 5
Engine 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 6
Engine 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 7
Engine 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 8
Engine 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 9
Engine 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 10
Total Engine Emissions (lb/hr) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Engine Emissions (lb/hr) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAP Limit (lb/hr)* |  | 1.85 | 5.43 | - | 0.022 | 0.022 | - | 0.059 | 0.0057 | 0.129
Engine Emission Cap Rate (lb/hr) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85.
IV. Annual Emission Limit (tpy)
Sheet ID | FIN | NOx | CO | PM | PM10 | PM2.5 | VOC | SO2 | H2SO4 | NH3
Engine 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engine 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 2
Engine 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 3
Engine 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 4
Engine 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 5
Engine 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 6
Engine 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 7
Engine 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 8
Engine 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 9
Engine 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FALSE | 10
Total Engine Emissions (tpy) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Engine Emissions (tpy) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAP Limit (tpy)* |  | 0.2775 | - | - | - | 0.0034 | - | 0.0088 | - | 0.0193
Engine Emission Cap Rate (tpy)** |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
**The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
End of sheet. Click here to move to the next sheet.

## Tanks
Diesel Tank(s) |  |  | Applicant Internal Comments | FALSE
This sheet details tank specifications and presents emission rates for up to ten diesel tanks. Instructions: 1. Select the number of tanks included in this project on the PI-1-PowerEngine sheet. Conditional formatting will grey out not applicable sections based on this response. 2. Complete all information below for each diesel tank included in this project. 3. Losses from each tank should be determined using the latest storage tank emission calculations or approved calculation software. Output files must be provided with the application. 4. Enter emission rate limits below to compare limits. Note: Section I represents the EPN and the emission limit for all tank(s) for this permit. The maximum lb/hr for each individual tank is listed in Section II. Individual tank emission limits cannot exceed the RAP limit. Section III compares the total and maxium emission limits of all tanks against the RAP limit. Total tank emission limits cannot exceed the RAP limit. |  |  | All comments must be deleted prior to application submittal.
.
I. Tank Cap Information
Requested Information | Response
Emission Point Number (EPN)
Source name
UTM zone
UTM coordinate - easting (meters)
UTM coordinate - northing (meters)
Number of tanks in this project: | 0
VOC - tanks standing losses cap (lb/hr) | 0
VOC - tanks filling losses cap (lb/hr) | 0
VOC - short-term tank cap (lb/hr) | 0
VOC - total standing + filling losses cap (tpy) | 0
A diesel tank will be used exclusively in supplying diesel to the engine(s). Due to the low volatility of diesel, along with the low overall capacity and throughput expected of the tank(s), default emission rates are used for this source. The default emission rates are expected to be representative so long as BACT is applied and use of the tank(s) is only to support operation of the engine(s). Acceptance of the proposed emission rates for the tank(s) is confirmed on the Special Conditions sheet.
II. Individual Tank Information
A. Tank1
Requested Information | Response | Limitations and Other Notes
FIN
Source name
UTM zone
UTM coordinate - easting (meters)
UTM coordinate - northing (meters)
Release height (ft) |  | minimum of 4 ft
Nominal capacity or working volume (gallons)
Maximum filling rate (gallons/hour)
Net annual throughput (gallons/year)
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy
B. Tank2 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
C. Tank3 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
D. Tank4 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
E. Tank5 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
F. Tank6 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
G. Tank7 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
H. Tank8 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
I. Tank9 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
J. Tank10 |  |  |  | TRUE
Requested Information | Response | Limitations and Other Notes |  | TRUE
FIN |  |  |  | TRUE
Source name |  |  |  | TRUE
UTM zone |  |  |  | TRUE
UTM coordinate - easting (meters) |  |  |  | TRUE
UTM coordinate - northing (meters) |  |  |  | TRUE
Release height (ft) |  | minimum of 4 ft |  | TRUE
Nominal capacity or working volume (gallons) |  |  |  | TRUE
Maximum filling rate (gallons/hour) |  |  |  | TRUE
Net annual throughput (gallons/year) |  |  |  | TRUE
VOC - standing losses (lb/hr) |  | maximum of 0.021 lb/hr |  | TRUE
VOC - filling losses (lb/hr) |  | maximum of 0.430 lb/hr |  | TRUE
VOC - total standing + filling losses (tpy) |  | maximum of 0.095 tpy |  | TRUE
.
III. Tank Emission Limit
Emission Type | Total Emissions | RAP Limit
VOC - standing losses (lb/hr) | 0 | maximum of 0.021 lb/hr* |  | FALSE
VOC - filling losses (lb/hr) | 0 | maximum of 0.430 lb/hr* |  | FALSE
VOC - total standing + filling losses (tpy) | 0 | maximum of 0.095 tpy** |  | FALSE
Emission Type | Max Emissions | RAP Limit
VOC - standing losses (lb/hr) | 0 | maximum of 0.021 lb/hr*
VOC - filling losses (lb/hr) | 0 | maximum of 0.430 lb/hr*
VOC - total standing + filling losses (tpy) | 0 | maximum of 0.095 tpy**
*The lb/hr maximums listed represent the combined maximum for all tanks at the site authorized by a RAP operating at any given time. For example, if one tank is in service, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr. If two tanks in service at the same time, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr.
**The tpy maximums listed represent the combined maximum for all tanks at the site authorized by a RAP. The tpy maximums listed represent the combined maximum for all tanks at the site authorized by a RAP. For example, if there is one tank, the maximum tpy emission rate is 0.095. If there are two tanks, the combined maximum tpy emission rate is 0.095.
End of sheet. Click here to move to the next sheet.

## Public Notice
Public Notice Applicability, Required Information, and Small Business Classification |  |  | Applicant Internal Comments | GRAY CF | RED CF | YEL CF
This sheet assists in this determination of public notice requirements and is not a replacement for 30 TAC Chapter 39 (Public Notice). The THSC §382.056 and corresponding rules in 30 TAC Chapter 39 (Public Notice) require that you publish a notice of intent to obtain a permit and notice of preliminary decision. Notices must be published in a newspaper of general circulation in the municipality where the proposed facility is or will be located (not applicable to alternative language notices). The notices must include a description of the facility and the fact that a person who may be affected by emissions from the facility may request a public hearing and any other information the TCEQ requires by rule. Signs must also be posted at the site in compliance with 30 TAC Chapter §39.604(c). Please review 30 TAC §39.426 for alternative language requirements for public participation processes that also may be applicable. Additional information regarding public notice such as an overview of requirements, an applicability table, and a list of some common errors that may cause renotice and delays in processing your application can be found at the link below: |  |  | All comments must be deleted prior to application submittal.
www.tceq.texas.gov/permitting/air/bilingual/how1_2_pn.html
Instructions: 1. Complete all questions below in the Public Notice Applicability section. A summary statement at the end will indicate if notice is required. 2. If public notice applies, complete Section II. 3. Complete all questions in the Small Business Classification section to determine eligibility.
I. Public Notice Applicability
A. Application Type
Is this an application for a new minor permit? |  | Yes
B. Is public notice required for this project as represented in this workbook? |  | Yes |  |  |  | TRUE
II. Public Notice Information
A. Contact Information
Enter the contact information for the person responsible for publishing. This is a designated representative who is responsible for ensuring public notice is properly published in the appropriate newspaper and signs are posted at the facility site. This person will be contacted directly when the TCEQ is ready to authorize public notice for the application.
Requested Information | Response
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Company Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
Enter the contact information for the Technical Contact. This is the designated representative who will be listed in the public notice as a contact for additional information.
Requested Information | Response
Prefix (Mr, Ms, Dr, etc.):
First Name:
Last Name:
Title:
Company Name:
Mailing Address:
Address Line 2:
City:
State:
ZIP Code:
Telephone Number:
Fax Number:
Email Address:
B. Public place Place a copy of the full application (including all of this workbook and all attachments) at a public place in the county where the facilities are or will be located. You must state where in the county the application will be available for public review and comment. The location must be a public place and described in the notice. A public place is a location which is owned and operated by public funds (such as libraries, county courthouses, or city halls) and cannot be a commercial enterprise. You are required to pre-arrange this availability with the public place indicated below. The application must remain available from the first day of publication through the designated comment period. If the application is submitted to the agency with information marked as Confidential, you are required to indicate which specific portions of the application are not being made available to the public. These portions of the application must be accompanied with the following statement: Any request for portions of this application that are marked as confidential must be submitted in writing, pursuant to the Public Information Act, to the TCEQ Public Information Coordinator, MC 197, P.O. Box 13087, Austin, Texas 78711-3087.
Requested Information | Response
Name of Public Place:
Physical Address:
Address Line 2:
City:
ZIP Code:
County:
Has the public place granted authorization to place the application for public viewing and copying?
Does the public place have Internet access available for the public?
C. Alternate Language Publication In some cases, public notice in an alternate language is required. If an elementary or middle school nearest to the facility is in a school district required by the Texas Education Code to have a bilingual program, a bilingual notice will be required. If there is no bilingual program required in the school nearest the facility, but children who would normally attend those schools are eligible to attend bilingual programs elsewhere in the school district, the bilingual notice will also be required. If it is determined that alternate language notice is required, you are responsible for ensuring that the publication in the alternate language is complete and accurate in that language.
Requested Information | Response
Is a bilingual program required by the Texas Education Code in the School District?
Are the children who attend either the elementary school or the middle school closest to your facility eligible to be enrolled in a bilingual program provided by the district?
If yes to either question above, list which language(s) are required by the bilingual program? |  |  |  | FALSE
Enter additional language, if applicable.
Enter additional language, if applicable.
Enter additional language, if applicable.
III. Small Business Classification
Complete this section to determine small business classification. If a small business requests a permit, agency rules [30 TAC §39.603(d)(1)(A)] allow for alternative public notification requirements if all of the following criteria are met. If these requirements are met, public notice does not have to include publication of the prominent (12 square inch) newspaper notice.
Requested Information | Response
Does the company (including parent companies and subsidiary companies) have fewer than 100 employees or less than $6 million in annual gross receipts?
Is the site a major source under 30 TAC Chapter 122, Federal Operating Permit Program? |  |  |  | FALSE
Are the site emissions of any individual air contaminant greater than or equal to 50 tpy? |  |  |  | FALSE
Are the site emissions of all air contaminants combined greater than or equal to 75 tpy? |  |  |  | FALSE
Small business classification: | [5 empty] | FALSE
IV. Plain Language Summary
Applications deemed administratively complete by May 1, 2022 must provide a plain language summary of the application to be posted on the TCEQ website. Templates can be found at the link below.
https://www.tceq.texas.gov/permitting/air/guidance/newsourcereview/nsrapp-tools.html
Requested Information | Response
Is a Plain Language Summary as required by 30 TAC § 39.405(k) provided with the application? |  |  |  |  | FALSE
Is a Plain Language Summary in an alternative language as required by 30 TAC § 39.426(c) provided with the application? |  |  |  |  | FALSE
End of sheet. Click here to move to the next sheet.

## Baseline
Baseline Emission Information | [8 empty] | Applicant Internal Comments
This sheet compiles baseline emission information for sources in this project for use in the federal applicability determination. Instructions: Enter the current sitewide potential to emit for each pollutant. Empty cells will be treated as 0. If this is a named source for PSD, the current sitewide PTE must include fugitive emissions. | [8 empty] | All comments must be deleted prior to application submittal.
Notes: 1. Baseline emissions years: -The baseline period is determined by a consecutive 24-month period and is not required to be on a calendar year basis. -You must use the same 24 months for a single pollutant. -The selected baseline period must be in the contemporaneous period. -Baseline actual emissions must be taken from the past 10 years. 2. Baseline emissions: -Enter the average over the baseline period. -The values cannot exceed the currently authorized emission rate. -The values must be relatively consistent with data from emissions inventory.
Subject | CO (tpy) | NOX (tpy) | PM (tpy) | PM10 (tpy) | PM2.5 (tpy) | VOC (tpy) | SO2 (tpy) | H2SO4 (tpy) | Applicant Internal Comments
Current Sitewide PTE (tpy) (all authorizations - does not include this project)
Baseline Emission Period (e.g. Feb 2022 - Jan 2023)
Engine1
Engine2
Engine3
Engine4
Engine5
Engine6
Engine7
Engine8
Engine9
Engine10
Tanks (All)
Total Baseline Emissions (tpy) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End of sheet. Click here to move to the next sheet.
index match | CO | NOX | PM | PM10 | PM2.5 | VOC | SO2 | H2SO4 | HIDE THIS ROW | nh3

## Federal Applicability
Federal Applicability Determination |  |  |  | Applicant Internal Comments | [7 empty] | Partial County List (12/2021) | Current Nonattainment Counties (12/2021), including counties designated maintenance (12/2021) |  |  |  |  | Table for threshold and offset look ups |  |  |  | Named Sources
This sheet determines federal applicability for this project. If the project requires netting, nonattainment NSR, and/or PSD review, it does not qualify for this RAP. |  |  |  | All comments must be deleted prior to application submittal. | [7 empty] | Anderson | County | Pollutant | Designation | Designation Text | Effective Date |  | Ozone | SO2 | PM10 | Other/Not Listed
Instructions: 1. Answer the general questions in Section I. 2. Complete Section II to determine if nonattainment NSR is required for the project as proposed. 3. Complete Section III to determine if PSD review is required for the project as proposed. 4. If nonattainment NSR, PSD review, or netting are required, then the project as proposed does not qualify for a RAP. Adjust the project to reduce emissions or apply for a case-by-case NSR permit using the Form PI-1. If nonattainment NSR, PSD review, and netting are not required, then continue to the next sheet. | [11 empty] | Freestone | Anderson | SO2 | nonattainment | nonattainment for SO2 | December 13, 2016 | Major Source - nonattainment |  | 100 |  | Carbon black plants (furnace process)
Notes: 1. Many of the cells will be populated automatically based on data entered on other sheets or questions. 2. The cells labeled "Determination" will guide you through this sheet. 3. More complex federal applicability review options are not allowed for this RAP: net-to-zero, retrospective review, incremental increases, and projected actuals/could have accommodated. 4. Additional information about federal applicability can be found at the link below: | [11 empty] | Howard | Bexar | ozone | moderate | moderate nonattainment for ozone | November 7, 2022 | Major Source - marginal | 100 |  |  | Charcoal production plants
https://www.tceq.texas.gov/assets/public/permitting/air/Guidance/NewSourceReview/fnsr_app_determ.pdf | [11 empty] | Hutchinson | Brazoria | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Major Source - moderate | 100 |  | 100 | Chemical process plants (other than ethanol by fermentation)
[12 empty] | Navarro | Chambers | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Major Source - serious | 50 |  | 70 | Coal cleaning plants (with thermal dryers)
I. General RAP Qualification Questions | [11 empty] | Panola | Collin | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Major Source - severe | 25 |  |  | Coke oven batteries
Requested Information | Response | [10 empty] | Rusk | Dallas | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Major Source - extreme | 10 |  |  | Fossil fuel-fired steam electric plants > 250 million BTUs per hour heat input
Confirm this project will have no affected sources upstream of the modified sources. | [5 empty] | FALSE | [5 empty] | Titus | Denton | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Netting Threshold - nonattainment |  | 40 |  | Fossil-fuel boilers (or combinations) totaling > 250 million BTUs per hour heat input
Confirm the following methods will not be used in the federal applicability analysis for this project: -net-to-zero; -retrospective review; -incremental increases; -projected actuals; -could have accommodated; or -decreases included in project emission increases. | [5 empty] | FALSE | [5 empty] | El Paso | El Paso | PM10 | moderate | moderate nonattainment for PM10 | November 6, 1991 | Netting Threshold - marginal | 40 |  |  | Fuel conversion plants
Are there any pending projects involving EPNs in this project? | [12 empty] | El Paso | ozone | moderate | moderate nonattainment for ozone | November 7, 2022 | Netting Threshold - moderate | 40 |  | 15 | Glass fiber processing plants
If yes, describe the proposed changes in the other pending projects. Limited to 300 characters. |  |  |  |  | FALSE | [7 empty] | Ellis | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Netting Threshold - serious | 5 |  | 15 | Hydrofluoric, sulfuric, or nitric acid plants
When was the most recent air authorization action affecting sources in this RAP project? Provide the date and a brief description of the change. Enter NA if there are no other air authorization actions affecting sources in this RAP project. Limited to 300 characters. | [12 empty] | Fort Bend | ozone | severe | severe nonattainment for ozone | November 7, 2022 | Netting Threshold - severe | 5 |  |  | Iron and steel mills
[13 empty] | Freestone | SO2 | nonattainment | nonattainment for SO2 | December 13, 2016 | Netting Threshold - extreme | 0 |  |  | Kraft pulp mills
II. Nonattainment NSR Applicability Summary | [12 empty] | Galveston | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Lime plants
A. Step 1: Determine if the site is in a nonattainment area for any criteria pollutant(s) or precursor(s). | [7 empty] | is an na county? | is el paso? | is partial SO2? |  |  | Harris | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Municipal incinerators capable of charging more than 250 tons of refuse per day
County (selected on the PI-1-PowerEngine sheet): | 0 | [5 empty] | 0 | FALSE | FALSE | FALSE |  |  | Howard | SO2 | nonattainment | nonattainment for SO2 | April 30, 2021 |  |  |  |  | Petroleum refineries
N/A |  |  |  |  | TRUE | [7 empty] | Hutchinson | SO2 | nonattainment | nonattainment for SO2 | April 30, 2021 |  |  |  |  | Petroleum storage and transfer units with total storage capacity above 300,000 barrels
Step 1 Determination: | This project will be located in an area currently designated attainment or unclassified for all criteria pollutants and precursors. Nonattainment NSR is not required. | [11 empty] | Johnson | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Phosphate rock processing plants
B. Step 2: Determine if the site is an existing major source. Compare the current sitewide PTE, including fugitive emissions at named sources, to the major source threshold for each criteria pollutant or precursor for which the area is nonattainment. |  |  |  |  | TRUE | [7 empty] | Kaufman | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Portland cement plants
Criteria Pollutant or Precursor | Current Sitewide PTE (tpy) all authorizations, excluding this project | Major Source Threshold (tpy) | Current Sitewide PTE ≥ Major Source Threshold? |  | TRUE | [7 empty] | Liberty | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Primary aluminum ore reduction plants
Ozone (as NOx) | 0 | 0 | Yes |  | TRUE |  | 0 | [5 empty] | Montgomery | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Primary copper smelters
Ozone (as VOC) | 0 | 0 | Yes |  | TRUE |  | 0 | [5 empty] | Navarro | SO2 | nonattainment | nonattainment for SO2 | April 30, 2021 |  |  |  |  | Primary lead smelters
PM10 | 0 | 0 | Yes |  | TRUE |  | 0 | [5 empty] | Panola | SO2 | nonattainment | nonattainment for SO2 | December 13, 2016 |  |  |  |  | Primary zinc smelters
SO2 | 0 | 0 | Yes |  | TRUE |  | 0 | [5 empty] | Parker | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Secondary metal production plants
Step 2 Determination: The site is currently a minor source for all evaluated criteria pollutants and precursors. |  |  |  |  | TRUE |  | ALL MINOR | [5 empty] | Rockwall | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Sintering plants
C. Step 3: Determine if the project emissions increase is a major source by itself. Compare the project emissions increase to the major source threshold corresponding to the area's nonattainment designation for each criteria pollutant or precursor. |  |  |  |  | TRUE | [7 empty] | Rusk | SO2 | nonattainment | nonattainment for SO2 | December 13, 2016 |  |  |  |  | Sulfur recovery plants
Criteria Pollutant or Precursor | Project Emissions Increase (tpy) (Project PTE - Baseline Actual Emissions) | Threshold (tpy) | Project Emissions Increase ≥ Threshold? |  | TRUE | [7 empty] | Tarrant | ozone | severe | severe nonattainment for ozone | November 7, 2022 |  |  |  |  | Taconite ore processing plants
Ozone (as NOx) | 0 | N/A | No |  | TRUE |  | major source - | N/A | 0 |  |  |  | Titus | SO2 | nonattainment | nonattainment for SO2 | December 13, 2016
Ozone (as VOC) | 0 | N/A | No |  | TRUE |  | major source - | N/A | 0 |  |  |  | Waller | ozone | severe | severe nonattainment for ozone | November 7, 2022
PM10 | 0 | N/A | No |  | TRUE |  | major source - | N/A | 0 |  |  |  | Wise | ozone | severe | severe nonattainment for ozone | November 7, 2022
SO2 | 0 | N/A | No |  | TRUE |  | major source - | N/A | 0
Step 3 Determination: The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. Nonattainment NSR is not required. Continue to the next section. |  |  |  |  | TRUE | FALSE |  |  | FALSE
III. PSD Applicability Summary
A. Step 1: Determine if the project is a named source.
Select the source type that most closely matches the facility in this application. If no source type applies, select "Other/Not Listed". Note: This list is based on 40 CFR § 51.166(b)(1)(i)(a).
Provide a short description of the facility, limited to 300 characters. |  |  |  |  | TRUE
Step 1 Determination: | Select and/or describe a source type above.
B. Step 2: Determine if the site is currently major by comparing the current sitewide PTE to the major source threshold. Read the step 1 determination above for information about including or excluding fugitive emissions in the PTE calculation.
Pollutant | Current Sitewide PTE (tpy) all authorizations, excluding this project | Major Source Threshold (tpy) | Current Sitewide PTE ≥ Major Source Threshold?
NOx | 0 | 100 | No |  |  |  | 0
CO | 0 | 100 | No |  |  |  | 0
SO2 | 0 | 100 | No |  |  |  | 0
PM | 0 | 100 | No |  |  |  | 0
PM10 | 0 | 100 | No |  |  |  | 0
PM2.5 | 0 | 100 | No |  |  |  | 0
VOC | 0 | 100 | No |  |  |  | 0
H2SO4 | 0 | 100 | No |  |  |  | 0
Step 2 Determination: The current sitewide PTE for each regulated pollutant is below the associated major source threshold. The site is currently a minor source. | [6 empty] | FALSE
C. Step 3: Determine if the project emissions increase is a major source by itself. Compare the project emissions increase of each pollutant to the associated major source threshold.
Pollutant | Project Emissions Increase (tpy) (Project PTE - Baseline Actual Emissions) | Threshold (tpy) | Increase ≥ Threshold? | [6 empty] | N/A
NOx | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | - | 0 | *Cells J53:J60: if the row is visible, returns 1 if increase is = or > threshold (summed in J61 for use in step 3 determination text)
CO | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | - | 0 | *Cells K53:K60: used only for nonattainment areas; returns 0 for regular criteria pollutants; returns 1 for nonattainment pollutants if increase is = or > threshold (summed in K61 for use in step 3 determination text)
SO2 | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | 0 | 0 | *Cells L53:L60: used only for nonattainment areas; returns 0 for nonattainment pollutants; returns 1 for regular criteria pollutants if increase is = or > threshold (summed in L61 for use in step 3 determination text)
PM | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | - | 0
PM10 | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | 0 | 0
PM2.5 | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | - | 0
VOC | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | 0 | 0
H2SO4 | 0 | 100 (major source threshold) | No |  | FALSE |  | 100 | 0 | - | 0
Step 3 Determination: The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. PSD review is not required. | [5 empty] | FALSE |  | FALSE | FALSE | FALSE
D. Step 4: Determine if the project emissions increase of the remaining regulated criteria and non-criteria pollutants is a major modification. Compare the project emissions increase for each remaining regulated pollutant to the associated significant level. |  |  |  |  | TRUE
Pollutant | Project Emissions Increase (tpy) (Project PTE - Baseline Actual Emissions) | Significant Level (tpy) | Increase ≥ Significant Level? |  | TRUE
NOx | 0 | 40 | No |  | TRUE |  |  | 0
CO | 0 | 100 | No |  | TRUE |  |  | 0
SO2 | 0 | 40 | No |  | TRUE |  |  | 0
PM | 0 | 25 | No |  | TRUE |  |  | 0
PM10 | 0 | 15 | No |  | TRUE |  |  | 0
PM2.5 | 0 | 10 | No |  | TRUE |  |  | 0
VOC | 0 | 40 | No |  | TRUE |  |  | 0
H2SO4 | 0 | 7 | No |  | TRUE |  |  | 0
Step 4 Determination: The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. PSD review is not required. |  |  |  |  | TRUE | FALSE |  | FALSE
End of sheet. Click here to move to the next sheet.

## BACT
Best Available Control Technology
This sheet lists the practices and controls which represent Best Available Control Technology (BACT) for each specific unit in this project. BACT is required by 30 TAC §116.111(a)(2)(C). Instructions: 1. Review the BACT with consideration given to the technical practicability and the economic reasonableness of reducing emissions from the facility. 2. Acceptance of the BACT for each unit is confirmed on the Special Conditions sheet.
I. Diesel-Fired Engines
NOx: Meeting EPA Tier 4I or 4F limits specified in NSPS Subpart IIII [40 CFR §60.4204(b), which references §60.4201(a), which references 40 CFR §1039.101, Table 1] and utilizing an SCR for engines equipped with an SCR. Have a non-resettable runtime meter.
VOC: Limited hours of operation, good operating practices, and meeting the limits of 40 CFR §1039.101, Table 1. Have a non-resettable runtime meter.
CO: Limited hours of operation, good operating practices, meeting the limits of 40 CFR §1039.101, Table 1, and utilizing an oxidation catalyst for engines equipped with one. Have a non-resettable runtime meter.
PM/PM10/PM2.5: Limited hours of operation and good operating practices. No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA Test Method 22 or equivalent. Have a non-resettable runtime meter.
SO2 and H2SO4: firing ultra-low sulfur diesel containing no more than 15 ppmw sulfur. Have a non-resettable runtime meter.
NH3 (for engines with SCR): Comply with the EPA-required manufacturer’s maintenance schedule which will ensure that the add-on control system functions as originally designed and comply with the 10 ppmv at 3% O2 emissions on a 1-hour block average pursuant to 30 TAC §117.2010(i)(2). Have a non-resettable runtime meter.
MSS: Minimize duration and occurrence of MSS activities.
II. Diesel Storage Tanks
VOC: Fixed roof with submerged fill. Uninsulated exterior surfaces exposed to the sun shall be white or aluminum.
MSS: Fixed roof tank send liquid to a covered vessel.
Note: Urea Storage Tanks
The tank is not considered an emission source because urea has a vapor pressure less than 0.01 mm Hg at 104⁰F (TCEQ's "When should a compound be considered an air contaminant" memo, September 19, 1996, linked below)
https://www.tceq.texas.gov/assets/public/permitting/air/memos/vapor4.pdf
End of sheet. Click here to move to the next sheet.

## AQA
Air Quality Analysis
This sheet provides the Air Quality Analysis summary which was performed by the TCEQ in support of the RAP: PowerEngine. Instructions: 1. Review the AQA. 2. Acceptance of the AQA is confirmed on the Special Conditions sheet.
To: Permit Staff Thru: Daniel Menendez, Manager Permit Support Section From: Dan Jamieson Permit Support Section Date: September 26, 2018 Subject: Air Quality Analysis Report – Power Generation Engine
I. Project Identification Information
An air quality analysis (AQA) was performed in support of the power generation engine readily available permit (RAP). This AQA report summarizes the model inputs and the results obtained from the analysis.
II. Report Summary
Generic modeling was conducted to determine maximum emission rates that yield predictions that are less than thresholds used in air quality impacts analyses. The thresholds include the following: for criteria pollutants – significant impact levels (SILs); for pollutants with a state property line (SPL) standard – two percent of the associated SPL standard; for pollutants with an Effects Screening Level (ESL) – ten percent of the associated ESL (ammonia and tank standing losses for diesel), two times the 1-hr ESL (tank filling for diesel), and the annual ESL (tank filling for diesel). Given that the threshold for 1-hr diesel is two times the ESL for tank filling, and that all receptors are being evaluated as non-industrial, the diesel tank filling emissions will be limited to no more than 24 hours per year total. The results are summarized below. Table 1 contains the generic modeling results. The 3-hr, 8-hr, 24-hr, and annual maximum predicted concentrations were derived by multiplying the 1-hr maximum predicted concentration by 0.9, 0.7, 0.4, and 0.08, respectively. Table 2 contains the thresholds used in the analysis for the various review types. Table 3 contains the maximum emission rates, both hourly and ton per year, for each pollutant. For pollutants with multiple short-term thresholds (24-hr or less) or evaluated for multiple review types (e.g., SO2), the maximum hourly emission rate represents the lowest emission rate. The tons per year values for engine emissions (all pollutants except diesel) are based on the maximum hourly emissions and 300 hours of operation, which is an operational limitation for this RAP.
Table 1. Generic Modeling Results
Source |  | Averaging Time | GLCmax (µg/m3) per lb/hr
Engine |  | 1-hr | 131.5
Engine |  | 3-hr | 118.35
Engine |  | 8-hr | 92.05
Engine |  | 24-hr | 52.6
Engine |  | Annual | 10.52
Tank |  | 1-hr | 7749
Tank |  | Annual | 620
Table 2. Analysis Thresholds
Pollutant | Averaging Time | Review Type | Threshold (µg/m3)
SO2 | 1-hr | SIL | 7.8
SO2 | 3-hr | SIL | 25
SO2 | 24-hr | SIL | 5
SO2 | Annual | SIL | 1
CO | 1-hr | SIL | 2000
CO | 8-hr | SIL | 500
PM10 | 24-hr | SIL | 5
PM2.5 | 24-hr | SIL | 1.2
PM2.5 | Annual | SIL | 0.2
NO2 | 1-hr | SIL | 7.5
NO2 | Annual | SIL | 1
SO2 | 1-hr | SPL | 14.3
H2SO4 | 1-hr | SPL | 1
H2SO4 | 24-hr | SPL | 0.3
NH3 | 1-hr | ESL | 18
NH3 | Annual | ESL | 9.2
Diesel (standing) | 1-hr | ESL | 100
Diesel (standing) | Annual | ESL | 10
Diesel (filling) | 1-hr | ESL | 2000
Diesel (filling) | Annual | ESL | 100
The justification for selecting the EPA’s interim 1-hr SO2 and 1-hr NO2 De Minimis levels was based on the assumptions underlying EPA’s development of the 1-hr SO2 and 1-hr NO2 De Minimis levels. As explained in EPA guidance memoranda, the EPA believes it is reasonable as an interim approach to use a De Minimis level that represents 4% of the 1-hr SO2 and 1-hr NO2 NAAQS.
www.epa.gov/sites/production/files/2015-07/documents/appwso2.pdf
www.tceq.texas.gov/assets/public/permitting/air/memos/guidance_1hr_no2naaqs.pdf
The PM2.5 De Minimis levels are the EPA recommended De Minimis levels. The use of the EPA recommended De Minimis levels is sufficient to conclude that a source will not cause or contribute to a violation of a PM2.5 NAAQS based on the analyses documented in EPA guidance and policy memoranda.
www.tceq.texas.gov/permitting/air/modeling/epa-mod-guidance.html
Table 3. Maximum Emission Rates
Pollutant |  | Averaging Time | Maximum Emission Rate (lb/hr or tpy)
SO2 |  | Short-term | 0.059
SO2 |  | Long-term | 0.0088
CO |  | Short-term | 5.43
PM10 |  | Short-term | 0.022
PM2.5 |  | Short-term | 0.022
PM2.5 |  | Long-term | 0.0034
NO2 |  | Short-term | 1.85
NO2 |  | Long-term | 0.2775
H2SO4 |  | Short-term | 0.0057
NH3 |  | Short-term | 0.129
NH3 |  | Long-term | 0.0193
Diesel (standing) |  | Short-term | 0.021
Diesel (standing) |  | Long-term | 0.09
Diesel (filling) |  | Short-term | 0.43
Diesel (filling) |  | Long-term | 1.17
III. Model Used and Modeling Techniques
SCREEN3 (Version 13043) was used. An emission rate of 1 lb/hr was used to predict a generic 1-hr concentration from an engine and a diesel tank. As noted above, the 1-hr maximum predicted concentration was multiplied by 0.9, 0.7, 0.4, and 0.08, to get generic predictions for the 3-hr, 8-hr, 24-hr, and annual averaging times, respectively. The generic concentrations were then used with the thresholds listed above in Table 2 to determine maximum emissions that yield predictions that are less than the thresholds. A. Land Use: Modeling was conducted using both rural and urban dispersion coefficients. The worst-case predictions were then used in the subsequent analyses. Flat terrain was used in the modeling analysis. Flat terrain is reasonable to use since it is consistent with typical site locations for these facilities and given that the maximum modeled predictions occur near the modeled source. B. Meteorological Data: The full meteorology option was selected in the modeling analysis. Additional model runs were conducted for the diesel tank using stability class 6 and a wind speed of 1.5 m/s. These selections are appropriate because stability class 6 is the worst-case stability and 1.5 m/s is the worst-case wind speed for low-level fugitive emissions. The National Weather Service considers wind speeds less than 1.5 m/s to be calm.
C. Receptor Grid: Receptors in the modeling analysis were generated using the automated distance option from 1 meter out to 50 kilometers. D. Building Wake Effects (Downwash): Two different cases were considered for the downwash analysis. Case 1 is a scenario in which there are no nearby structures; only the engine housing structure is used as input. The dimensions for a typical engine housing structure were used (horizontal dimension of approximately 30 feet by 10 feet, and a vertical dimension of 10 feet). Case 2 is a scenario that considers a nearby structure larger than the engine housing structure. The dimensions for the nearby structure are representative of a typical building (horizontal dimension of approximately 40 feet by 40 feet, and a vertical dimension of 25 feet). The worst-case predictions were then used in the subsequent analyses. Building downwash was not considered for the diesel tank. The diesel tank emissions were characterized as an area source and downwash is not applicable for area source modeling.
IV. Modeling Emissions Inventory
The power generation engine has emissions from a stack and emissions that are fugitive in nature. The determination of the modeled source parameters was based on a review of previously submitted permit applications for power generation engine projects and selecting representative source parameters. Each modeled source is further described below, and the modeled source parameters are summarized in Tables 4 and 5. Engine: This modeled source represents the engine stack and it was modeled as a point source using the parameters listed in Table 4. Tank: This modeled source represents fugitive emissions from the diesel tank and it was modeled as an area source using the parameters listed in Table 5. The horizontal dimensions of the area source are based on the dimensions for a typical engine housing structure. The release height was based on how emissions may escape the engine housing structure – primarily from vents located along the sides of the engine housing structure near the top, as well as from any doors that may be opened.
Table 4. Point Source Parameter Information
Source | Release Height (ft) | Exit Temperature (°F) | Exit Velocity (ft/sec) | Exit Diameter (ft)
Engine | 25 | 828 | 168.7 | 0.66
Table 5. Area Source Parameter Information
Source | Release Height (ft) | Length (ft) | Width (ft)
Tank | 4 | 30 | 7
To account for conversion of NOx to NO2, a factor of 0.9 was used in the analysis. A factor of 0.9 is the maximum default value for ARM2, and the use of ARM2 is consistent with EPA guidance for conducting a Tier 2 screening approach. When the maximum diesel emissions that yield predictions that are less than the thresholds were determined, a fugitive adjustment factor of 0.6 was applied to the generic concentrations of the tank. This is consistent with TCEQ guidance for these types of sources. For the 1-hr NO2 analysis, emissions from the power generation engine were evaluated with an annual average emission rate, consistent with EPA guidance for evaluating intermittent emissions. The emissions from the engine are based on 300 hours per year of operation.
End of sheet. Click here to move to the next sheet.

## Tox
Toxicology Review
This sheet provides the toxicology health effects review of diesel emissions which was performed by the TCEQ in support of the RAP: PowerEngine. Instructions: 1. Review the memo. 2. Acceptance of the memo is confirmed on the Special Conditions sheet.
To: Permit Staff Air Permits Division From: Tiffany Bredfeldt, Ph.D. Toxicology Division Subject: Health effects review of emissions from the Readily Available Permit for Engine Power Generation (Tox Control No. RAP 001)
As requested, we conducted a health effects review of air emissions from the Readily Available Permit (RAP) for engine power generation. The RAP is a type of New Source Review (NSR) permit for a facility that is granted based upon emissions calculations, equipment, and site- specific parameters. Thus, permits of this type include parameters that must be satisfied before the application is submitted to the agency. The purpose of this RAP is to authorize the operation of up to ten engines and the associated diesel storage tanks for power generations. The engines and tanks may be in a greenfield or an existing site. Sources permitted under this RAP will be considered all new to the site. The goal of the following health effects review is to evaluate the modeled emissions from engines and the diesel storage tank predicted to occur at this facility and whether these emissions would be of concern to human health and welfare (odor and vegetation).
Generic screen modeling (SCREEN3) was conducted to determine maximum emission rates that yield predictions that are less than thresholds used in air quality impacts analyses. The threshold for ammonia emissions from tank standing loss is set at 10% of the associated Effects Screening Level (ESL). The thresholds for diesel emissions from tank loading are set at two times the 1-hour (hr) ESL and the annual ESL. The corresponding maximum emission rates are limited to 0.129 lb/hr and 0.0193 tpy for ammonia and are limited to 0.43 lb/hr and 1.17 tpy for diesel. The sources contemplated in this permitting action are limited to 10 diesel-fired engines and the associated diesel storage tanks (up to 10). Only one tank may be loaded at a time and the combined loading of all tanks must be less than 24 hours per year. Given the conservatism in the model, all receptors are being evaluated as non-industrial receptors, the limitations on this permit, and the overall impacts for ammonia and diesel meet their respective threshold, these emissions are allowable.
In conclusion, we do not anticipate any short- or long-term adverse health effects to occur among the general public as a result of exposure to the proposed emissions from this facility. If you have further questions, please contact me at the following phone number 512-239-1799 or e-mail address tiffany.bredfeldt@tceq.texas.gov.
End of sheet. Click here to move to the next sheet.

## CND
Special Conditions
This sheet contains the draft permit prepared by the TCEQ for RAP: PowerEngine projects. Instructions: 1. Review the Special Conditions. During the technical review, APD staff will convert this sheet to a Word document which will be a part of the permit. 2. Electronically sign this document at the end, indicating agreement with the statement.
I. Special Conditions
Section Title | Special Condition Language
N/A | 1. This permit authorizes emissions only from those emission points listed in the attached table entitled “Emission Sources - Maximum Allowable Emission Rate,” and the facilities covered by this permit are authorized to emit subject to the emission rate limits on that table and other operating conditions specified in this permit. Also, this permit authorizes the emissions from planned maintenance, startup, and shutdown.
Federal and State Applicability | 2. The facility shall comply with applicable requirements of the EPA regulations on Standards of Performance for New Stationary Sources, 40 CFR Part 60:
Federal and State Applicability | A. Subpart A: General Provisions
Federal and State Applicability | B. Subpart IIII: Standards of Performance for Stationary Compression Ignition Internal Combustion Engines
Federal and State Applicability | 3. The facility shall comply with applicable requirements of the EPA regulations on National Emission Standards for Hazardous Air Pollutants for Source Categories, 40 CFR Part 63:
Federal and State Applicability | A. Subpart A: General Provisions
Federal and State Applicability | B. Subpart ZZZZ: National Emission Standard for Hazardous Air Pollutants for Stationary Reciprocating Internal Combustion Engines
Federal and State Applicability | 4. This condition applies to sources in the Houston-Galveston-Brazoria or the Dallas-Fort Worth ozone non-attainment areas. The applicable counties are Brazoria, Chambers, Fort Bend, Galveston, Harris, Liberty, Montgomery, Waller, Collin, Dallas, Denton, Ellis, Johnson, Kaufman, Parker, Rockwall, and Tarrant. The condition also applies to sources in Wise County emitting 50 tpy NOx or greater. There shall be no operations of a diesel engine for testing or maintenance between 6:00 am and noon, except:
Federal and State Applicability | A. For specific manufacturer’s recommended testing requiring a run of over 18 consecutive hours; or
Federal and State Applicability | B. To verify reliability of emergency equipment (e.g., emergency generators or pumps) immediately after unforeseen repairs. Routine maintenance such as an oil change is not considered to be an unforeseen repair.
Emission Standards and Operating Specifications | 5. All engines authorized through the RAP program shall not exceed a combined 300 hours of operation per rolling 12-month period.
Emission Standards and Operating Specifications | 6. A non-resettable run time meter shall be installed on each engine.
Emission Standards and Operating Specifications | 7. Each engine and after-treatment control device (if present) shall be operated and maintained according to the manufacturer's emission-related written instructions.
Emission Standards and Operating Specifications | 8. Startup and shutdown of the engine(s), where the after-treatment control device is not controlling emissions, shall not exceed 30 minutes per event.
Emission Standards and Operating Specifications | 9. No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA Test Method (TM 22) or equivalent.
Emission Standards and Operating Specifications | 10 .The following requirements apply to the site:
Emission Standards and Operating Specifications | A. No more than one diesel tank may be filled at the same time.
Emission Standards and Operating Specifications | B. The combined diesel tank filling operations must not occur more than 24 hours per rolling 12-month period.
Emission Standards and Operating Specifications | C. The combined sitewide maximum diesel tank(s) VOC emission limit is 0.43 pounds per hour.
Emission Standards and Operating Specifications | 11. Fuel fired in each engine is limited to diesel containing no more than 15 ppmw sulfur.
Recordkeeping | 12. The following records shall be kept at the plant for the life of the permit. All records required in this permit shall be made available at the request of personnel from the TCEQ, EPA, or any air pollution control agency with jurisdiction:
Recordkeeping | A. A copy of this permit.
Recordkeeping | B. The initial permit application and subsequent representations submitted to the TCEQ.
Recordkeeping | C. A copy of each engine's manufacturer’s design and operation specifications and all emission-related maintenance requirements.
Recordkeeping | 13. The following information shall be maintained by the holder of this permit in a form suitable for inspection for a period of five years after collection and shall be made available upon request to representatives of the TCEQ, EPA, or any local air pollution control program having jurisdiction:
Recordkeeping | A. Hours of operation kept on a monthly and rolling 12-month basis. Hours of operation shall be summed for all engines at the site authorized through the RAP program.
Recordkeeping | B. Records of fuel delivery indicating date, quantity of fuel delivered, and duration of tank filling activity for each tank.
Recordkeeping | C. Records of the fuel sulfur content. The analysis may be performed by the permit holder, service contractor, the fuel vendor, or any other qualified agency.
Recordkeeping | D. Records of engine maintenance, including replacement of control system components, media, and sensors, if present.
Recordkeeping | E. Records of visible emissions, opacity observations, and any corrective actions taken to demonstrate compliance with Special Condition No. 9
Acronyms | 40 CFR Part 60: Title 40 Code of Federal Regulations Part 60
Acronyms | 30 TAC: Title 30 Texas Administrative Code
Acronyms | EPA: U.S. Environmental Protection Agency
Acronyms | ppmw: parts per million by weight
Acronyms | RAP: Readily Available Permit
Acronyms | TCEQ: Texas Commission on Environmental Quality
II. Applicant Confirmation
I have reviewed and agree to the following representations in this workbook: BACT; emission rates; the draft permit; the Air Quality Analysis; and all other representations made in this application workbook. In addition, this workbook is submitted as part of my application and accurately represents my proposed project.
Confirm that you agree with the statement above by electronically signing (typing) your name here.
End of sheet. Click here to move to the Project Summary sheet.

## Project Summary
Project Summary |  |  |  |  | FORMULA | FORMULA | FORMULA | RED
This sheet gathers information from all over the workbook and organizes it in a way that is easier for permit reviewers to copy and paste into their review documents.
Administrative Project Information
Requested Information | Response
Company |  |  |  |  | 0
City |  |  |  |  | 0
County |  |  |  |  | 0
Project Type | Initial |  |  |  | Yes
Facility Name |  |  |  |  | 0
Permit Number | TBD |  |  |  | *Update if Amendments are added
RN |  |  |  |  | 0
CN |  |  |  |  | 0
Site Name |  |  |  |  | 0
Project Overview
0
Emission Summary
Air Contaminant | Current Allowable Emission Rates (tpy) | Project Allowable Emission Rates (tpy) | Change in Allowable Emissions (tpy) | Project Emissions Increase (Baseline Actual to Allowable) (tpy)
NOx | 0 | 0 | 0 | 0
CO | 0 | 0 | 0 | 0
SO2 | 0 | 0 | 0 | 0
PM | 0 | 0 | 0 | 0
PM10 | 0 | 0 | 0 | 0
PM2.5 | 0 | 0 | 0 | 0
VOC | 0 | 0 | 0 | 0
H2SO4 | 0 | 0 | 0 | 0
NH3 | 0 | 0 | 0 | 0
Public Notice Information
The permit reviewer has verified that all public notice requirements were satisfactorily completed for the proposed permit. The permit holder was required to publish Notice of Receipt of Application and Intent to Obtain Permit “First Public Notice” under 30 TAC §39.418. The permit holder was also required to publish Notice of Application and Preliminary Decision “Second Public Notice” under 30 TAC §39.419. The notices were consolidated under 30 TAC §39.603(d). The newspaper notice listed the following pollutants, as required under 30 TAC §39.411(e)(10): carbon monoxide, oxides of nitrogen, sulfur dioxide, organic compounds, particulate matter including particulate matter with diameters of 10 microns or less and 2.5 microns or less, ammonia, and sulfuric acid. |  |  |  |  | Yes
Emission Sources
Unit Type | FINs
Diesel-fired engine
Diesel Storage Tank
Requirements
Federal Applicability | Prevention of Significant Deterioration | The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. PSD review is not required. |  |  | Step 3 Determination: The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. PSD review is not required. | The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. PSD review is not required. |  | FALSE
| Nonattainment |  |  |  | Step 3 Determination: The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. Nonattainment NSR is not required. Continue to the next section. | The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. Nonattainment NSR is not required. Continue to the next section. | The project emissions increase for each evaluated pollutant and/or precursor is below the threshold. Nonattainment NSR is not required. | 0
General Requirements | Permit fee |  |  |  | 0
Impacts Analysis | Is there a school within 3000 ft of any facility authorized by this permit? |  |  |  | 0
Maximum Allowable Emission Rate Table
This table lists the maximum allowable emission rates and all sources of air contaminants on the applicant’s property covered by this permit. The emission rates shown are those derived from information submitted as part of the application for permit and are the maximum rates allowed for these facilities, sources, and related activities. Any proposed increase in emission rates may require an application for a modification of the facilities covered by this permit.
EPN | Source Name | Air Contaminant | Short-Term Emission Rate (lb/hr) | Annual Emission Rate (tpy)
0 | 0 | NOx | 0 | 0
|  | CO | 0 | 0
|  | PM | 0 | 0
|  | PM10 | 0 | 0
|  | PM2.5 | 0 | 0
|  | VOC | 0 | 0
|  | SO2 | 0 | 0
|  | H2SO4 | 0 | 0
|  | NH3 | 0 | 0
0 | 0 | VOC | 0 | 0
End of workbook. Click here to move to the Instructions sheet.

## Reference (hidden)
TCEQ 20952, Version 2.1
Updated Date: | 2023-12-12
Project Manager | Sandra Juarez
Team Members | Jordyn Winter, Jett Koen
Previous Date: | Version 2 - 11/22
*Future Proof Note | *CND 4 - check for updates to Nonattainment 117.10 (C) + Brazoria, Chambers, Fort Bend, Galveston, Harris, Liberty, Montgomery, and Waller Counties. +117.2130 **There may be a coming change for Public Notice regarding proof of display (noted during demo)
Last Updated: | October 7, 2022 | <linked to Fed applicability | https://www.federalregister.gov/documents/2022/10/07/2022-20460/determinations-of-attainment-by-the-attainment-date-extensions-of-the-attainment-date-and |  | https://www.federalregister.gov/documents/2022/10/07/2022-20458/determinations-of-attainment-by-the-attainment-date-extensions-of-the-attainment-date-and | see table in [Fed Ap]tab PI1:T31 ish
Future Update Ideas: | Consider moving Reference to Reference Tab (ie- Fed appiablity updates in P1:T31)
Accessiblity Note | Blank cells are used in this workbook. "Helper" cells add information to tables are included that might be merged with other cells to make text easier to read.
Name | Title V Threshold (TPY) | NA Threshold NOX and VOC (TPY) | NA Threshold PM10 (TPY) | FIN Code | FIN | Source Name | NOx lb/hr | NOx tpy | CO lb/hr | CO tpy | PM lb/hr | PM tpy | PM10 lb/hr | PM10 tpy | PM2.5 lb/hr | PM2.5 tpy | VOC lb/hr | VOC tpy | SO2 lb/hr | SO2 tpy | H2SO4 lb/hr | H2SO4 tpy | NH3 lb/hr | NH3 tpy | grey out code - ENGINES based if FIN is blank AND #-o-Engine < Engine# | [15 empty] | Engine Source Drop Down Menu Options | Engine Source Notes | Counter | # of engines authorize | Engine FINs - Unique ID | Engine FINs - Raw | Engine FINs - Clean | # of tanks authorized | Tank FINs - Unique ID | Tank FINs - Raw | Tank FINs - Clean
Anderson | 100 | 249 | 249 | total | Engines (All) | All engines at the site authorized by a RAP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Pollutant | Name Header | CO | NOx | PM | PM10 | PM2.5 | SO2 | VOC | Pb | H2S | TRS | Reduced sulfur compounds (including H2S) | H2SO4 | Fluoride (excluding HF) |  | vendor guarantee | must provide documentation with example and specs | 1 | 0 | 0 | 0 |  | 0 | 0 | 0
Andrews | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Current Sitewide PTE (tpy) | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | AP-42 Table 3.3-1 | must use most current version | 2 |  | 0 | 0 |  |  | 0 | 0
Angelina | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Baseline Emission Years | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | testing data | must provide documentation and stack test data | 3 |  | 0 | 0 |  |  | 0 | 0
Aransas | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE1 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 1 | federal standard(s) | must provide citation | 4 |  | 0 | 0 |  |  | 0 | 0
Archer | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE2 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 2 |  |  | 5 |  | 0 | 0 |  |  | 0 | 0
Armstrong | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE3 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 3 |  |  | 6 |  | 0 | 0 |  |  | 0 | 0
Atascosa | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE4 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 4 |  |  | 7 |  | 0 | 0 |  |  | 0 | 0
Austin | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE5 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 5 |  |  | 8 |  | 0 | 0 |  |  | 0 | 0
Bailey | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE6 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 6 |  |  | 9 |  | 0 | 0 |  |  | 0 | 0
Bandera | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE7 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 7 |  |  | 10 |  | 0 | 0 |  |  | 0 | 0
Bastrop | 100 | 249 | 249 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE8 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 8 | [5 empty] | Eng FIN list: |  |  |  | Tk FIN list:
Baylor | 100 | 249 | 249 |  | Tanks (all) | [19 empty] | ENGINE9 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 9
Bee | 0 | 249 | 249 |  |  | Totals All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | ENGINE10 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 10
Bell | 100 | 249 | 249 | [21 empty] | TANKS (ALL) | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
Bexar | 100 | 249 | 249
Blanco | 100 | 249 | 249 | [21 empty] | test | FALSE
Borden | 100 | 249 | 249
Bosque | 100 | 249 | 249
Bowie | 100 | 249 | 249
Brazoria | 100 | 100 | 249
Brazos | 100 | 249 | 249
Brewster | 100 | 249 | 249
Briscoe | 100 | 249 | 249 | CAP vs Default
Brooks | 100 | 249 | 249 | Cap check | Title | standard
Brown | 100 | 249 | 249 | engine | Cap | cap
Burleson | 100 | 249 | 249 | tank | Cap | cap
Burnet | 100 | 249 | 249
Caldwell | 100 | 249 | 249
Calhoun | 100 | 249 | 249
Callahan | 100 | 249 | 249
Cameron | 100 | 249 | 249 | ENGINE Summary Logic
Camp | 100 | 249 | 249 |  | NOx | CO | PM | PM10 | PM2.5 | VOC | SO2 | H2SO4 | NH3 | CHECK
Carson | 100 | 249 | 249 | CHECK1 -Total Engine Emissions (lb/hr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cass | 100 | 249 | 249 | CHECK2 -Max Engine Emissions (lb/hr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Castro | 100 | 249 | 249 | CHECK3- Max Engine Emissions(tpy) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chambers | 100 | 100 | 249 | CHECK4- Total Engine Emissions (tpy) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cherokee | 100 | 249 | 249
Childress | 100 | 249 | 249 | ENGINE Summary Text Logic (lb/hr)
Clay | 100 | 249 | 249 | C1- FAIL | *If the Total Engine Emissions exceeds the RAP limit but Max Engine Emissions does not, engines must be operated to comply with the RAP limit. The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85.
Cochran | 100 | 249 | 249 | C2- FAIL | *Individual operational hours is in exceedence of the RAP conditions.
Coke | 100 | 249 | 249 | 1ENGINE | *Individual engine complies withthe RAP conditions.
Coleman | 100 | 249 | 249 | General - lb/hr | *The lb/hr maximums listed represent the combined maximum for all engines at the site authorized by a RAP operating at any given time. For example, if one engine is operating, the maximum NOx lb/hr emission rate is 1.85. If two engines are operating at the same time, the maximum combined NOx lb/hr emission rate is 1.85.
Collin | 100 | 100 | 249 | ENGINE Summary Text Logic (tpy)
Collingsworth | 100 | 249 | 249 | C3-FAIL | **If the Total Engine Emissions exceeds the RAP limit but Max Engine Emissions does not, engines must be operated to comply with the RAP limit. The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
Colorado | 100 | 249 | 249 | General - tpy | **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
Comal | 100 | 249 | 249 | 1ENGINE | **Individual engine complies withthe RAP conditions.
Comanche | 100 | 249 | 249 | General - tpy | **The tpy maximums listed represent the combined maximum for all engines at the site authorized by a RAP. For example, if there is one engine, the maximum NOx tpy emission rate is 0.2775. If there are two engines, the combined maximum NOx tpy emission rate is 0.2775.
Concho | 100 | 249 | 249
Cooke | 100 | 249 | 249
Coryell | 100 | 249 | 249 | BACT SC B17
Cottle | 100 | 249 | 249 | TRUE
Crane | 100 | 249 | 249
Crockett | 100 | 249 | 249 | TODAY
Crosby | 100 | 249 | 249 | 2023-12-11
Culberson | 100 | 249 | 249
Dallam | 100 | 249 | 249
Dallas | 100 | 100 | 249 | Tank Sum Text Logic (lb/hr)
Dawson | 100 | 249 | 249 | C1- FAIL | *If the Total Tank Emissions exceeds the RAP limit but Max Tank Emissions does not, tanks must comply with the RAP limit. The lb/hr maximums listed represent the combined maximum for all tanks at the site authorized by a RAP operating at any given time. For example, if one tank is in service, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr. If two tanks in service at the same time, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr.
Deaf Smith | 100 | 249 | 249 | General - lb/hr | *The lb/hr maximums listed represent the combined maximum for all tanks at the site authorized by a RAP operating at any given time. For example, if one tank is in service, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr. If two tanks in service at the same time, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr.
Delta | 100 | 249 | 249 | Tank Sum Text Logic (tpy)
Denton | 100 | 100 | 249 | C3-FAIL | **If the Total Tank Emissions exceeds the RAP limit but Max Tank Emissions does not, tanks must comply with the RAP limit. The tpy maximums listed represent the combined maximum for all tanks at the site authorized by a RAP. For example, if there is one tank, the maximum tpy emission rate is 0.095. If there are two tanks, the combined maximum tpy emission rate is 0.095.
DeWitt | 100 | 249 | 249 | General - tpy | **The tpy maximums listed represent the combined maximum for all tanks at the site authorized by a RAP. The tpy maximums listed represent the combined maximum for all tanks at the site authorized by a RAP. For example, if there is one tank, the maximum tpy emission rate is 0.095. If there are two tanks, the combined maximum tpy emission rate is 0.095.
Dickens | 100 | 249 | 249
Dimmit | 100 | 249 | 249 | *If the Total Tank Emissions exceeds the RAP limit but Max Tank Emissions does not, tanks must comply with the RAP limit. The lb/hr maximums listed represent the combined maximum for all tanks at the site authorized by a RAP operating at any given time. For example, if one tank is in service, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr. If two tanks in service at the same time, the maximum combined standing emissions is 0.021 lb/hr and the maximum combined filling emissions is 0.430 lb/hr.
Donley | 100 | 249 | 249
Duval | 100 | 249 | 249
Eastland | 100 | 249 | 249
Ector | 100 | 249 | 249
Edwards | 100 | 249 | 249
Ellis | 100 | 100 | 249
El Paso | 100 | 249 | 100
Erath | 100 | 249 | 249
Falls | 100 | 249 | 249
Fannin | 100 | 249 | 249
Fayette | 100 | 249 | 249
Fisher | 100 | 249 | 249
Floyd | 100 | 249 | 249
Foard | 100 | 249 | 249
Fort Bend | 100 | 100 | 249
Franklin | 100 | 249 | 249
Freestone | 100 | 249 | 249
Frio | 100 | 249 | 249
Gaines | 100 | 249 | 249
Galveston | 100 | 100 | 249
Garza | 100 | 249 | 249
Gillespie | 100 | 249 | 249
Glasscock | 100 | 249 | 249
Goliad | 100 | 249 | 249
Gonzales | 100 | 249 | 249
Gray | 100 | 249 | 249
Grayson | 100 | 249 | 249
Gregg | 100 | 249 | 249
Grimes | 100 | 249 | 249
Guadalupe | 100 | 249 | 249
Hale | 100 | 249 | 249
Hall | 100 | 249 | 249
Hamilton | 100 | 249 | 249
Hansford | 100 | 249 | 249
Hardeman | 100 | 249 | 249
Hardin | 100 | 249 | 249
Harris | 100 | 100 | 249
Harrison | 100 | 249 | 249
Hartley | 100 | 249 | 249
Haskell | 100 | 249 | 249
Hays | 100 | 249 | 249
Hemphill | 100 | 249 | 249
Henderson | 100 | 249 | 249
Hidalgo | 100 | 249 | 249
Hill | 100 | 249 | 249
Hockley | 100 | 249 | 249
Hood | 100 | 249 | 249
Hopkins | 100 | 249 | 249
Houston | 100 | 249 | 249
Howard | 100 | 249 | 249
Hudspeth | 100 | 249 | 249
Hunt | 100 | 249 | 249
Hutchinson | 100 | 249 | 249
Irion | 100 | 249 | 249
Jack | 100 | 249 | 249
Jackson | 100 | 249 | 249
Jasper | 100 | 249 | 249
Jeff Davis | 100 | 249 | 249
Jefferson | 100 | 249 | 249
Jim Hogg | 100 | 249 | 249
Jim Wells | 100 | 249 | 249
Johnson | 100 | 100 | 249
Jones | 100 | 249 | 249
Karnes | 100 | 249 | 249
Kaufman | 100 | 100 | 249
Kendall | 100 | 249 | 249
Kenedy | 100 | 249 | 249
Kent | 100 | 249 | 249
Kerr | 100 | 249 | 249
Kimble | 100 | 249 | 249
King | 100 | 249 | 249
Kinney | 100 | 249 | 249
Kleberg | 100 | 249 | 249
Knox | 100 | 249 | 249
Lamar | 100 | 249 | 249
Lamb | 100 | 249 | 249
Lampasas | 100 | 249 | 249
La Salle | 100 | 249 | 249
Lavaca | 100 | 249 | 249
Lee | 100 | 249 | 249
Leon | 100 | 249 | 249
Liberty | 100 | 100 | 249
Limestone | 100 | 249 | 249
Lipscomb | 100 | 249 | 249
Live Oak | 100 | 249 | 249
Llano | 100 | 249 | 249
Loving | 100 | 249 | 249
Lubbock | 100 | 249 | 249
Lynn | 100 | 249 | 249
McCulloch | 100 | 249 | 249
McLennan | 100 | 249 | 249
McMullen | 100 | 249 | 249
Madison | 100 | 249 | 249
Marion | 100 | 249 | 249
Martin | 100 | 249 | 249
Mason | 100 | 249 | 249
Matagorda | 100 | 249 | 249
Maverick | 100 | 249 | 249
Medina | 100 | 249 | 249
Menard | 100 | 249 | 249
Midland | 100 | 249 | 249
Milam | 100 | 249 | 249
Mills | 100 | 249 | 249
Mitchell | 100 | 249 | 249
Montague | 100 | 249 | 249
Montgomery | 100 | 100 | 249
Moore | 100 | 249 | 249
Morris | 100 | 249 | 249
Motley | 100 | 249 | 249
Nacogdoches | 100 | 249 | 249
Navarro | 100 | 249 | 249
Newton | 100 | 249 | 249
Nolan | 100 | 249 | 249
Nueces | 100 | 249 | 249
Ochiltree | 100 | 249 | 249
Oldham | 100 | 249 | 249
Orange | 100 | 249 | 249
Palo Pinto | 100 | 249 | 249
Panola | 100 | 249 | 249
Parker | 100 | 100 | 249
Parmer | 100 | 249 | 249
Pecos | 100 | 249 | 249
Polk | 100 | 249 | 249
Potter | 100 | 249 | 249
Presidio | 100 | 249 | 249
Rains | 100 | 249 | 249
Randall | 100 | 249 | 249
Reagan | 100 | 249 | 249
Real | 100 | 249 | 249
Red River | 100 | 249 | 249
Reeves | 100 | 249 | 249
Refugio | 100 | 249 | 249
Roberts | 100 | 249 | 249
Robertson | 100 | 249 | 249
Rockwall | 100 | 100 | 249
Runnels | 100 | 249 | 249
Rusk | 100 | 249 | 249
Sabine | 100 | 249 | 249
San Augustine | 100 | 249 | 249
San Jacinto | 100 | 249 | 249
San Patricio | 100 | 249 | 249
San Saba | 100 | 249 | 249
Schleicher | 100 | 249 | 249
Scurry | 100 | 249 | 249
Shackelford | 100 | 249 | 249
Shelby | 100 | 249 | 249
Sherman | 100 | 249 | 249
Smith | 100 | 249 | 249
Somervell | 100 | 249 | 249
Starr | 100 | 249 | 249
Stephens | 100 | 249 | 249
Sterling | 100 | 249 | 249
Stonewall | 100 | 249 | 249
Sutton | 100 | 249 | 249
Swisher | 100 | 249 | 249
Tarrant | 100 | 100 | 249
Taylor | 100 | 249 | 249
Terrell | 100 | 249 | 249
Terry | 100 | 249 | 249
Throckmorton | 100 | 249 | 249
Titus | 100 | 249 | 249
Tom Green | 100 | 249 | 249
Travis | 100 | 249 | 249
Trinity | 100 | 249 | 249
Tyler | 100 | 249 | 249
Upshur | 100 | 249 | 249
Upton | 100 | 249 | 249
Uvalde | 100 | 249 | 249
Val Verde | 100 | 249 | 249
Van Zandt | 100 | 249 | 249
Victoria | 100 | 249 | 249
Walker | 100 | 249 | 249
Waller | 100 | 100 | 249
Ward | 100 | 249 | 249
Washington | 100 | 249 | 249
Webb | 100 | 249 | 249
Wharton | 100 | 249 | 249
Wheeler | 100 | 249 | 249
Wichita | 100 | 249 | 249
Wilbarger | 100 | 249 | 249
Willacy | 100 | 249 | 249
Williamson | 100 | 249 | 249
Wilson | 100 | 249 | 249
Winkler | 100 | 249 | 249
Wise | 100 | 100 | 249
Wood | 100 | 249 | 249
Yoakum | 100 | 249 | 249
Young | 100 | 249 | 249
Zapata | 100 | 249 | 249
Zavala | 100 | 249 | 249

## ProcessFlow (hidden)
Process Flow Diagram-THIS TAB IS NOT UTILIZED IN THE CURRENT VERSION, BUT REMAINS INCASE OPTION BECOME ALLOWABLE | [8 empty] | Applicant Internal Comments
This sheet provides an example process flow diagram, that can be updated with the applicable information for this project. Alternatively, applicants can provide their own process flow diagrams attached with their application. A process flow diagram is required for all projects. It should identify raw materials to be used in the process, all major processing steps and major equipment items, individual emission points associated with each process step, the location and identification of all emission abatement devices, and the location and identification of all waste streams (including wastewater streams that may have associated air emissions). Instructions: 1. Review the process flow diagram below. 2. Update as necessary to make it representative of your project. 3. If needed, you may delete this example and provide an attached diagram with your application. | [8 empty] | All comments must be deleted prior to application submittal.
The Figure below is an example of the process- Ex) Diesel fuel is received from a truck and routed to storage tank 1 to 10. Tank emissions are emitted from EPN TANK1 to TANK10. The fuel is routed to Engine 1 to Engine 10. Engine exhaust is emitted from EPN ENGINE1 to ENGINE10. Electricity is produced by the engine.
|  | Tank emissions EPN: |  |  |  | Engine exhaust EPN:
|  | ↑ up arrow |  |  |  | ↑ up arrow
Diesel fuel from truck | → right arrow | FIN: TANK1 to TANK10 | → right arrow | Fuel flow | → right arrow | FIN: ENGINE1 to ENGINE10 | → right arrow | Electricity
End of sheet. Click here to move to the next sheet.

## Current PTE (hidden)
Current Potential to Emit - THIS TAB IS NOT UTILIZED IN THE CURRENT VERSION, BUT REMAINS INCASE AMENDMENTS BECOME ALLOWABLE | [10 empty] | Applicant Internal Comments
This sheet summarizes the current annual emissions from each source represented in this workbook. Instructions: 1. For new sources - leave associated cell in that row blank. 2. For existing sources - enter the current ton per year emission rate from the current MAERT for each source modified with this project. | [10 empty] | All comments must be deleted prior to application submittal.
ID | Source Name | Current NOX (tpy) | Current CO (tpy) | Current PM (tpy) | Current PM10 (tpy) | Current PM2.5 (tpy) | Current VOC (tpy) | Current SO2 (tpy) | Current H2SO4 (tpy) | Current NH3 (tpy) | Applicant Internal Comments
0 | All engines at the site authorized by a RAP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total | No data | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
End of sheet. Click here to move to the next sheet.
=IF(OR([@[Project Allowable Emission Rates (tpy)]]=0,[@[Project Allowable Emission Rates (tpy)]]-index('Baseline'!$B$19:$I$19,match(PS_Emissions_Summary[@Air Contaminant],'Current PTE'!$C$20:$K$20<0),0,[@[Project Allowable Emission Rates (tpy)]]-Baseline!C$19)