## Owner Data
2022
TX# | Dam Name | Latitude | Longitude | OWNER/Operator | Operation & Maintenance/Rehab Schedule |  | Annual O&M Cost | Method of Finance
TX04779 | PALMETTO BEND DAM | 28.8896 | -96.5797 | Lavaca-Navidad River Authority | 1. Measure, record, and broadcast water surface elevations hourly during flood operations. | Daily | 1087484.7 | Water Customer Water Supply Contracts | ProRata Share
[5 empty] | 2. Determine reservoir inflow. | Daily |  | Formosa Plastics | 0.5534
[5 empty] | 3. Record spillway and ROW discharges and check for presence of seepage, movement and/or changes of seepage, settlement, sloughing of embankments. | Daily |  | City of Corpus Christi | 0.4223
[5 empty] | 4. Record pertinent information in the Operating Log. | Daily |  | Inteplast Group | 0.0139
[5 empty] | 5. Maintain security of the dam and associated appurtenances. | Daily |  | City of Point Comfort | 0.0024
[5 empty] | 6. Read and record weather gage data. | Daily |  | Calhoun County Port Authority | 0.008
[5 empty] | 7. Make required changes in gates and valves. | Daily
[5 empty] | 8. Check instrumentation reading schedules and collect data as required. | Daily
[5 empty] | 9. Check seepage and toe drains as appropriate. | Daily
[5 empty] | 10. Monitor ROW discharge. | Daily
[5 empty] | 11. Check spillway control panel for gate position. | Daily
[5 empty] | 12. Review early warning system information and record pertinent data. | Daily
[5 empty] | 13. Clean parking lots and downstream area of trash. | Daily
[5 empty] | 14. Record data from the east lean concrete and west ROW seepage area. | Daily
[5 empty] | 15. Examine stilling basin and downstream channel. | Daily
[5 empty] | 16. Check concrete surfaces for signs of cracking or deterioration; also check after sustained use. | Daily
[5 empty] | 17. Check the flow from boil and test well in east drain. | Daily
[5 empty] | 1. Record readings at special interest piezometers, embankment drain outlets, and toe drains. Also record readings at | Weekly
[5 empty] | any instruments recommended by the Dam Safety Consultant. | Weekly
[5 empty] | 2. Check and exercise the backup generator, record output readings. | Weekly
[5 empty] | 3. Check seepage areas, toe drains. | Weekly
[5 empty] | 4. Satisy bay & estuary requirements | Weekly
[5 empty] | 1. Check condition of and note any changed condition of: | Monthly
[5 empty] | a. Crest of dam. | Monthly
[5 empty] | b. Upstream and downstream faces of dam. | Monthly
[5 empty] | c. Visible portions of dam foundation. | Monthly
[5 empty] | d. Abutment contacts. | Monthly
[5 empty] | e. Spillway and M&I Galleries. | Monthly
[5 empty] | f. Stilling basin. | Monthly
[5 empty] | g. Reservoir area. | Monthly
[5 empty] | h. Drainage systems. | Monthly
[5 empty] | i. Measuring devices. | Monthly
[5 empty] | j. Security and safety devices. | Monthly
[5 empty] | k. Inspect for oil, gas, or chemical leaks. | Monthly
[5 empty] | l. All drop structures. | Monthly
[5 empty] | m. East and west dike (for erosion) and sloughing. | Monthly
[5 empty] | n. East and west drain (for erosion) and sloughing. | Monthly
[5 empty] | o. Fuel supplies for Spillway Generator. This will be checked as needed and will increase in frequency as appropriate | Monthly
[5 empty] | during hurricane season. | Monthly
[5 empty] | p. Communicate with Instrumentation and Electronics (I&E) section on Early Warning performance. | Monthly
[5 empty] | q. All batteries, flashlights, emergency food supplies, as needed. Increase frequency as appropriate during hurricane season. | Monthly
[5 empty] | r. Area 1 fence lines and gates. | Monthly
[5 empty] | 2. Record and report all rainfall, inflows and releases. | Monthly
[5 empty] | 3. Record readings on all piezometers, embankment drains, toe drains and east drop structure. | Monthly
[5 empty] | 1. Check hoist deck gauge and battery. | Quarterly
[5 empty] | 2. Check manual gauge in probe well and flush piping due to sediment. | Quarterly
[5 empty] | 3. Check and service gallery pumps, gans, and lighting. | Quarterly
[5 empty] | 4. Check and spot prime damaged paint areas on handrails. | Quarterly
[5 empty] | 5. Mow maximum section, east and west dike, and drop structure slopes. | Quarterly
[5 empty] | 6. Check and run all spillway boats used for reservoir operations; check pumps, lifejackets and lights. | Quarterly
[5 empty] | 1. Check downstream ROW and spillway channels by boat. Take pictures of all changes. | Semi-Annually
[5 empty] | 2. Measure and record readings on inclinometers. | Semi-Annually
[5 empty] | 3. Measure and record readings on gallery wells. | Semi-Annually
[5 empty] | 4. Measure ansd record readings on observation wells. | Semi-Annually
[5 empty] | 5. Monitor and perform aquatic vegetation control in lake. | Semi-Annually
[5 empty] | 1. Operate, grease and service all gate hoists and motors on spillway, ROW and M&I structures. Lubricate all wire ropes | Annually
[5 empty] | and shafts. | Annually
[5 empty] | 2. Contract for the measurement of all settlement and deflection measurement points (embankments, spillway and outlet works). | Annually
[5 empty] | 3. Inspect and if needed, clean, prime, paint and repair handrails, hoist, hoist motors, stoplogs and spreader bar/lifting beam | Annually
[5 empty] | at spillway and river outlet areas. | Annually
[5 empty] | 4. Operate and perform inspection of all underwater gates, stilling basin, upstream and downstream side of gates, M&I, and | Annually
[5 empty] | river outlet gates. | Annually
[5 empty] | 5. Check and restock limestone, gravel road material, riprap, 4- to 6-inch limestone rock, rock 1- to 4-inches, and base | Annually
[5 empty] | material. | Annually
[5 empty] | 6. Hold periodic staff meetings in regard to storms, floods, disasters and accidents. | Annually
[5 empty] | 7. Participate in training on cardiopulmonary resuscitation and Basic First Aid or Emergency Care Attendant (ECA). | Annually
[5 empty] | 8. Exercise all 12 spillway gates to full travel. Check function of limit switches. Calibrate controls. | Annually
[5 empty] | 9. Exercise emergency gate opening using the drill (only one gate). | Annually
[5 empty] | 10. Check condition of interior and exterior of outlet conduits. | Annually
[5 empty] | 11. Check electrical conduits, pullboxes and switches. | Annually
[5 empty] | 12. Review SOP. | Annually
[5 empty] | 13. Perform safety walk through of the spillway and related operating structures. | Annually
[5 empty] | 14. Inspect, locate, relocate, replace and/or remove lake markers, buoys and boating hazards. | Annually
[5 empty] | 15. Load test emergency generator. | Annually
[5 empty] | 16. Do an aerial survey of the Project. | Annually
[5 empty] | 1. Participate in comprehensive review. | Each 5 Years
[5 empty] | 1. Examine intake structure and stilling basin, which are normally underwater. | Annually
[5 empty] | 2. Conduct unbalanced head tests on all spillway gates at least once every 6 years, during a period of high reservoir level. | Each 6 Years
Note that, when these tests have otherwise been performed as a function of normal reservoir operations within a 6 year
period, they do not need to be repeated.
Testing should be done in the following sequence:
Open the gate 10 percent, then close. If the gate has not been operated in the past year, the 10 percent test should be
made in progressive steps as follows:
a. Barely open (crack) the gate so that it will produce additional leakage, then close.
b. Open the gate 1 inch, then close.
c. Open the gate 6 inches, then close.
d. Open the gate 10 percent, then close. If 10 percent gate opening is not possible because of downstream restrictions,
open it as far as possible, then close.
[5 empty] | 1. As necessay check automatic gate operations. | AS Needed
[5 empty] | 2. Document and report any unusual conditions which occur such as new seeps, weeps, unusual readings, and slumps/sloughs. | AS Needed
[5 empty] | 3. Spray noxious weeds. | AS Needed
[5 empty] | 4. Spray or remove trees on dam embankment and drains. | AS Needed
[5 empty] | 5. Mow weeds and grasses within Area 1. | AS Needed
[5 empty] | 6. Complete other work as specified or directed by the Dam Operator and/or LNRA's Administrative Office. | AS Needed
[5 empty] | 7. Report any unsafe condition. | AS Needed
[5 empty] | 8. Provide general public information and assistance. | AS Needed
[5 empty] | 9. Perform maintenance painting. | AS Needed
[5 empty] | 10. Attend group safety meetings and perform job related tailgate safety meetings. | AS Needed
[5 empty] | 11. Service all equipment according to manufacturer's instructions. | AS Needed
[5 empty] | 12. Inspect, maintain and repair embankment slopes, terraces and slope protection (riprap, rockfill and soil cement). | AS Needed
[5 empty] | 13. Collect and submit instrumentation recordings and other data in accordance with the Dam Safety Consultant. | AS Needed
[5 empty] | 14. Report operational information to Dam Safety Consultant, in accordance with flood control regulations and operating | AS Needed
[5 empty] | procedures. | AS Needed
[5 empty] | 15. During times of emergencies, maintain communication with proper authorities. | AS Needed
[5 empty] | 16. Follow an operating and maintenance schedule to ensure a properly functioning system. | AS Needed
[5 empty] | 17. Provide training to select LNRA employees to operate and maintain the dam and reservoir in an emergency situation. | AS Needed
SCHEDULE FOR PERIODIC MONITORING & DATA COLLECTION
[5 empty] | Daily Visual Inspection | Daily
[5 empty] | Annual Survey of Embankment Measurement Points | Once Per Year
[5 empty] | Annual Survey of Concrete Structures Measurement Points | Once Per Year
[5 empty] | Annual Survey of ROW Stilling Basin Headwall Movement | Once Per Year
[5 empty] | Semi-Annual Data Collection of Inclinometer Readings | Twice Per Year
[5 empty] | Monthly Data Collection of East Drain Standpipe Piezometers and Main Dam Piezometers | Monthly
[5 empty] | Semi-Annual Data Collection of East & West Drain Observation Wells (OW-300 Series) | Twice Per Year
[5 empty] | Semi-Annual Data Collection of Outlying Observation Wells (ow-80 Series) | Twice Per Year
[5 empty] | Daily Data Collection on all NEW Seepage Flows | Daily
[5 empty] | Weekly Data Collection on all EXISTING Seepage Flows | Weekly
[5 empty] | Daily, Weekly or Monthly Data Collection of all Foundation Drain Depths to Water | As Directed
REHABILITATION SCHEDULE
[5 empty] | Spillway Gate Coating and Gate Seal Replacement | 15 years
[5 empty] | Spillway Stoplog Coating and Stoplog Seal Replacement | As Required
[5 empty] | Spillway Gate Cable Replacement | As Required
[5 empty] | Spillway Gate Arm Pinion Rehabilitation | As Required
[5 empty] | Spillway Hoist Deck Equipment Refurbishment | As required
[5 empty] | Spillwat Hoist Deck Equipment Coating | 15 Year
[5 empty] | Spilllway Gantry Crane Refurbishment | 15 Year or As Required
[5 empty] | Spillway Gantry Crane Coating | 15 Years
[5 empty] | Spillway Auxillary Generator Refurbishment | 20 Years
[5 empty] | Spillway Gate Automated Control System Refurbishment | 20 Years or As Needed
[5 empty] | Embankment Repair | As Needed
[5 empty] | Dam Instrumentation Refurbishment | As Needed
[5 empty] | Dam Embankment Armmorment Rehabilitation | 50 Years or As Needed
[5 empty] | Spillway Inlet Channel Armmorment Rehabilitation | 50 Years or AS Needed
[5 empty] | Concrete Structure Repair | As Needed