## Sheet1
Groundwater CT Study Template (MS Excel version)
This Template is used to determine the Minimum Specified Residual (MSR)
at a plant using free chlorine to achieve a 4.0-log viral inactivation
| PWS Name: | PWS ID No.:
| Plant Name: | Date Completed:
1 | Total capacity (maximum) of all storage tanks at this site |  |  | gallons
2 | Minimum volume/water level | gallons (or feet)
3 | Maximum volume/water level | gallons (or feet)
4 | Actual Min/Max Ratio (line 2 divided by line 3)
5 | Maximum allowable ratio | 0.5
6 | Allowable ratio (minimum of line 4 and line 5)
7 | Allowable Volume (line 1 times line 6) |  |  | gallons
8 | Baffling Factor |  | 0.1
9 | Effective Volume (line 7 times line 8) |  |  | gallons
10 | Total capacity (maximum) of the wells feeding these tanks | gpm
11 | Total capacity (maximum) of all the service pumps fed by these tanks | gpm
12 | Flow rate (minimum of line 10 and line 11) |  |  | gpm
13 | T10 for this site (line 9 divided by line 12) |  |  | minutes
14 | CT required for a 4-log viral inactivation if the water temperature is at least 10oC and the pH is not greater than 9.5. |  | 6 | mg/L-min
Assuming that you are using free chlorine, your water temperature does not drop below 10oC (50oF), and the pH is always below 9.5 . . . The Minimum Specified Residual (MSR) for this Entry Point will be: (line 14 divided by line 13) |  |  |  | mg/L
If the T10 is less than 1.5 minutes, the TCEQ cannot approve a Minimum Specified Residual for this site because it would be greater than 4.0 mg/L under worst-case operating conditions.
Note: Enter data in the yellow cells. The values in the orange cells will automatically be calculated by the spreadsheet.
Groundwater CT Study Template (Schematic)
| PWS Name: | PWS ID No.:
| Plant Name: | Date Completed:
Simple Plant Schematic Showing Injection and Monitoring Points
Note on G10: Enter the amount of water that is available when the tank is full and all the pumps are off. This is the volume of water that can be stored between the floor of the storage tank and its overflow. This capacity is generally less than the nominal tank capacity because it does not include the volumes between the overflow pipe and the tank roof. If there is a battery of tanks at the plant, enter the sum of the tank capacities. Do not include the volume of water stored in tanks where the water enters and leaves the tank through the same pipe.
Note on E11: Enter the minimum volume (or water depth) that exists in the tank during periods of peak demand. This water level is usually located somewhere between the level where the well pump turns on and the level where the low-level cutoff switch turns off the service pumps.
Note on E12: Enter the total volume (or water level) that exists when the tank is completely full and all the pumps are off. This water level is the distance between the tank floor and the overflow.
Note on E19: Enter the maximum combined capacity of all the wells that feed this storage tank or battery of tanks.
Note on E20: Enter the maximum combined capacity of all the service pumps that take suction from this storage tank or battery of tanks.