## Tier I BACT - Combustion
Press TAB to move cells. Press UP or DOWN ARROW in column A to read through Unit Types.
Current Tier I BACT Requirements: Combustion Sources
Version APDG6498v2
Last Revision Date: June 4, 2019
Instructions: Use the small arrow in cell A5 to sort, filter, and search the unit type list. Be sure to scroll to the right to view all pollutants.
Unit Type | Date of Last Update | MSS | PM | VOC | Exempt Solvent | NOx | SO2 | CO | NH3 | H2S | H2SO4 | Hg | HCl
Boiler: hazardous waste | 2018-10-01 | Minimizing the duration of these activities and operating the facility in accordance with best management practices and good air pollution control practices | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE | Meet 30 TAC 335 and 40 CFR 63 Subpart EEE
Boiler: liquid and gas fuel, > 40 MMBtu/hr | 2018-10-01 | Minimizing the duration of these activities and operating the facility in accordance with best management practices and good air pollution control practices | Less than 5% opacity. Good combustion practices. | Good combustion practices. | No data | Specify fuel type(s) to be fired. When firing natural gas: 0.01 lb/MMBtu When firing plant fuel gas: 0.015 lb/MMBtu Note: plant fuel gas may contain up to 75% natural gas. Specifics: <50% H2; > 920 Btu/dscf. Emission limits typically achieved using dry-low NOx combustors, limiting fuel consumption, SCR, and/or water or steam injection. Specify technique(s). Fuel oil firing limited to 760 hours/yr. | Firing pipeline quality natural gas When firing fuel gas, fuel must contain no more than 10 grains of total sulfur per 100 dry standard cubic feet. When firing liquid fuel, fuel must contain no more than 0.05% sulfur by weight with a limit of 720hrs/yr. Good combustion practices. | 50 ppmv at 3% O2 achieved by good combustion practices, oxidation catalyst, and/or maintenance of the boiler. Specify technique(s). | 10 ppmvd at 3% O2 achieved by controlling the NH3 injection system to minimize NH3 slip. | Firing pipeline quality natural gas When firing fuel gas, fuel must contain no more than 10 grains of total hydrogen sulfide per 100 dry standard cubic feet. When firing liquid fuel, fuel must contain no more than 0.05% sulfur by weight with a limit of 720hrs/yr. Good combustion practices. | Firing pipeline quality natural gas When firing fuel gas, fuel must contain no more than 10 grains of total sulfur per 100 dry standard cubic feet. When firing liquid fuel, fuel must contain no more than 0.05% sulfur by weight with a limit of 720hrs/yr. Good combustion practices. | No data | No data
Boiler: liquid and gas fuel, ≤ 40 MMBtu/hr | 2018-10-01 | Minimizing the duration of these activities and operating the facility in accordance with best management practices and good air pollution control practices | Case by case analysis required. | Case by case analysis required. | No data | Case by case analysis required. | Case by case analysis required. | Case by case analysis required. | Case by case analysis required. | Case by case analysis required. | Case by case analysis required. | No data | No data
Boiler: solid fuel | 2018-10-01 | Minimizing the duration of these activities and operating the facility in accordance with best management practices and good air pollution control practices | Filterable PM will be controlled using fabric filters (baghouses), cyclone separator and/or electrostatic precipitator. Provide details of technology to be utilized. Biomass: increasing the residence time, providing sufficiently high combustion temperatures, and using a fuel with high organic content. The filterable and total PM emission limits are 0.012 lb/MMBtu and 0.025 lb/MMBtu, respectively. Any other fuel type: Case by case analysis required. | Biomass: ideal combustion practices including high temperatures, adequate excess air and residence time, and optimal fuel/air mixing during combustion. The system design for the fluidized bed boiler provides the operating environment required to facilitate complete combustion to achieve a VOC emission rate not exceeding 0.01 lb/MMBtu, and averaging not more than 0.008 lb/MMBtu on an annual basis. Any other fuel type: Case by case analysis required. | No data | Biomass: A hybrid SNCR/SCR system will reduce NOX emissions to less than 0.075 lb/MMBtu on a 30 day and annual rolling average. Any other fuel type: Case by case analysis required. | Biomass: low sulfur content ranging from 0.01% to 0.03% by weight to limit the level of SO2 emissions from the boiler. Additional control of emissions will be achieved through the use of dry sorbent injection as needed. These techniques will control SO2 emissions to less than 0.025 lb/MMBtu Any other fuel type: Case by case analysis required. | Biomass: good combustion practices including high temperatures, adequate excess air and residence time, and optimal fuel/air mixing during combustion. These techniques will minimize CO emissions to a level of 0.075 lb/MMBtu on a 30-day rolling average and 0.30 lb/MMBtu as an hourly maximum. Use of an Oxidation catalyst will minimize CO emissions to 0.075 lb/MMBtu. Any other fuel type: Case by case analysis required. | Biomass: use of operational instrumentation systems to limit the aqueous ammonia injection rate such that the 30-day rolling average NH3 slip emissions from the SNCR/SCR system will not exceed 15 ppmvd at 7% oxygen. Any other fuel type: Case by case analysis required. | No data | Biomass: fuels have low sulfur content ranging from 0.01% to 0.03% by weight which limits the level of H2SO4 emissions from the boiler. Additional control of emissions will be achieved through the use of dry sorbent injection as needed to control H2SO4 emissions to less than 0.001 lb/MMBtu. Any other fuel type: Case by case analysis required. | No data | Biomass: Dry sorbent injection will be used as needed to control the emissions of hydrogen chloride to 0.02 lb/MMBtu Any other fuel type: Case by case analysis required.
coal loading | 2018-10-01 | Same as normal operation BACT requirements. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | 70% reduction- Storage pile load-in, stockpiles, and roads: Typically achieved by water sprays 85% reduction-Transfer points : typically achieved by foam and/or surfactant. 90% reduction-Receiving and unloading : typically achieved by foam sprays and enclosures Conveying :typically enclosed (50 -90% reduction); chemical sprays (80 - 90% reduction); full enclosure (90+ %) Crushing : typically enclosed Screening : typically enclosed; partial enclosure and water sprays 95% reduction -Loading: typically achieved by chemical wetting and enclosure, chemical wetting and choke feeding, or fabric filter on silo. Specify technique. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Control: bag filter/baghouse | 2018-10-01 | Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Opacity shall not exceed 5% and/or no visible emissions from each stack or vent. 99% reduction or outlet grain loading of 0.01 gr/dscf, typically achieved with fabric filters. Specify technique. | No data | No data | No data | No data | No data | No data | When firing fuel gas, fuel must contain no more than 10 grains of total sulfur per 100 dry standard cubic feet. | No data | No data | No data
Control: flare | 2018-10-01 | Same as normal operation BACT requirements. | No data | Meets requirement of 40 CFR 60.18. Destruction Efficiency: 99% for certain compounds up to three carbons, 98% otherwise. No flaring of halogenated compounds is allowed. Flow monitor required. Composition or BTU analyzer may be required. | No data | Provide proposal and justification. Flow monitor will be required. Composition or BTU analyzer may be required. | Provide proposal and justification. Flow monitor will be required. Composition or BTU analyzer may be required. | Provide proposal and justification. Flow monitor will be required. Composition or BTU analyzer may be required. | No data | No data | No data | No data | No data
Control: vapor combustor | 2018-10-01 | Same as normal operation BACT requirements. | No data | 99% destruction efficiency. Monitor temperature. Perform initial test. | No data | No data | No data | No data | No data | When firing liquid fuel, fuel must contain no more than 0.05% sulfur by weight with a limit of 720hrs/yr. | No data | No data | No data
Cooling tower | 2018-10-01 | Same as normal operation BACT requirements. | Drift < 0.001% achieved by drift eliminators | Non-contact design. Monthly monitoring of VOC in water per Appendix P or approved equivalent (assume all VOC stripped out) Repair identified leaks as soon as possible, but before next scheduled shutdown, or shutdown triggered by 0.08 ppmw cooling water VOC concentration | No data | No data | No data | No data | No data | No data | No data | No data | No data
Crusher | 2018-10-01 | No downtime since water sprays shall be operational and in good repair prior to the start of operations. Opacity requirements same as normal operation BACT requirements. | Coal: 90% reduction, typically enclosed 70% reduction at inlet and outlet of all crushers, at all screens and material transfer points, Typically water sprays 70% reduction All stockpiles and active work areas – typically water spray systems 0.05 g/dscm or 7% opacity Any stack emissions unless using a wet scrubber. Establish pressure of gas stream and scrubbing liquid flow rate during initial performance test. (NSPS) 10% opacity if constructed, modified, or reconstructed prior to 4/22/2008; 7% opacity if constructed, modified, or reconstructed on or after 4/22/2008 -Any transfer point on belt conveyors or any screen (NSPS) 15% opacity if constructed, modified, or reconstructed prior to 4/22/2008; 12% opacity if constructed, modified, or reconstructed on or after 4/22/2008 - Any crusher with no capture system (NSPS) No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six -minute period as determined using EPA TM 22 or equivalent - From the crusher, screens, engine/generator, transfer points on belt conveyors, material storage or feed bins, stockpiles, internal roads, or work areas. | No data | No data | No data | If using liquid fuel, it shall have a maximum 0.3% sulfur content. | No data | No data | Good combustion practices. | No data | No data | No data
Dryer | 2018-10-01 | No additional controls required for MSS operations beyond normal operation BACT requirements. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Firing pipeline quality sweet natural gas and good combustion practices. | Firing pipeline quality sweet natural gas and good combustion practices. | Firing pipeline quality sweet natural gas and good combustion practices. | Firing pipeline quality sweet natural gas and good combustion practices. Specify if firing alternate fuel. | Firing pipeline quality sweet natural gas and good combustion practices. | Firing pipeline quality sweet natural gas and good combustion practices. | No data | No data | No data | No data | No data
Engine: emergency, diesel | 2018-10-01 | Minimize duration and occurrence of MSS activities. | Meeting the requirements of 40 CFR Part 60, Subpart IIII. Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight). Limited to 100 hrs./yr. of non-emergency operation. Have a non-resettable runtime meter. No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA TM 22 or equivalent | Meeting the requirements of 40 CFR Part 60, Subpart IIII. Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight). Limited to 100 hrs./yr. of non-emergency operation. Have a non-resettable runtime meter. | No data | Meeting the requirements of 40 CFR Part 60, Subpart IIII. Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight). Limited to 100 hrs./yr. of non-emergency operation. Have a non-resettable runtime meter. | Meeting the requirements of 40 CFR Part 60, Subpart IIII. Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight). Limited to 100 hrs./yr. of non-emergency operation. Have a non-resettable runtime meter. | Meeting the requirements of 40 CFR Part 60, Subpart IIII. Firing ultra-low sulfur diesel fuel (no more than 15 ppm sulfur by weight). Limited to 100 hrs./yr. of non-emergency operation. Have a non-resettable runtime meter. | No data | No data | No data | No data | No data
Engine: internal combustion engine, spark ignited | 2018-10-01 | Minimize duration and occurrence of MSS activities. NOx and CO: provide case-by-case analysis. Pipelines: VOC in compressor, suction line, and discharge line may be vented. | Good combustion practices. Limited to firing fuels which meet the requirements of 40 CFR §72.2 or §80.1604. No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA TM 22 or equivalent | 1.0 g/bhp-hr achieved through good combustion practices. | No data | 1.0 g/bhp-hr for engines less than 500 hp, 0.5 g/bhp-hr for engines greater than or equal to 500 hp. 0.7 g/bhp-hr is acceptable with vendor guarantee. Achieved through good combustion practices. Provide detail about engine size and numeric value. Rich burn engine: catalytic converter required and no liquid fuel allowed except for a limited number of backup hours. Provide detail of fuel and number of hours requested. | Good combustion practices. Limited to firing fuels which meet the requirements of 40 CFR §72.2 or §80.1604. | 3.0 g/hp-hr achieved through good combustion practices. | No data | Good combustion practices. Limited to firing fuels which meet the requirements of 40 CFR §72.2 or §80.1604. | Good combustion practices. Limited to firing fuels which meet the requirements of 40 CFR §72.2 or §80.1604. | No data | No data
Fugitives: building | 2018-10-01 | Same as normal operation BACT requirements. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Fugitives: piping and equipment leak | 2018-10-01 | Same as normal operation BACT requirements. Best management practices (BMPs) will be used to minimize emissions, including using proper design of fuel delivery and handling, good air pollution control practices, and safe operating practices. Estimate fugitive emissions of sources such as natural gas, diesel, and ammonia. Leak detection and repair program as required for minimizing VOC leaks. | No data | Provide details about applicable option: 1. Uncontrolled VOC emissions < 10 tpy - no control required 2. 10 tpy < uncontrolled VOC emissions < 25 tpy - 28M LDAR program. 75% credit. 3. Uncontrolled VOC emissions > 25 tpy - 28VHP LDAR program. 97% credit for valves, 85% for pumps and compressors. 4. VOC vapor pressure < 0.002 psia - no inspection required, no fugitive emissions expected. For emissions of chlorine and other approved odorous compounds: AVO inspection twice per shift. | No data | No data | No data | No data | AVO inspection | AVO inspection twice per shift | No data | No data | No data
Furnace: > 40 MMBtu/hr | 2018-10-01 | No additional controls required for MSS operations beyond normal operation BACT requirements. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | No data | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. Burners with the best NOx performance given the burner configuration and gaseous fuel used. Specify the proposed emission rate (performance is an annual average) and provide justification if NOx>0.01 lb/MMBtu. Cost data must be submitted for SCR if firing rate is > 300 MMBtu/hr and burner is >0.01 lb/MMBtu. CEMS required for 100 MMBtu/hr or greater. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | Good combustion practices. 50 ppmv corrected to 3% O2. | No data | No data | No data | No data | No data
Furnace: ≤ 40 MMBtu/hr | 2018-10-01 | No additional controls required for MSS operations beyond normal operation BACT requirements. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | No data | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. Burners with the best NOx performance given the burner configuration and gaseous fuel used. Specify the proposed emission rate (performance is an annual average) and provide justification if NOx>0.01 lb/MMBtu. | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | Good combustion practices. 50 ppmv corrected to 3% O2. | No data | No data | No data | No data | No data
Heater > 40 MMBtu/hr | 2018-10-01 | Same as normal operation BACT requirements. | Maximum opacity 5% | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | No data | Burners with the best NOx performance given the burner configuration and gaseous fuel used. Specify the proposed emission rate (performance is an annual average) and provide justification if NOx>0.01 lb/MMBtu. Cost data must be submitted for SCR if firing rate is > 300 MMBtu/hr and burner is >0.01 lb/MMBtu. CEMS required for 100 MMBtu/hr or greater. | Maximum 0.6% sulfur content any liquid fuel or 5 grains for pipeline quality sweet natural gas. Provide details. | 50 ppmv corrected to 3% O2 | No data | No data | No data | No data | No data
Heater ≤ 40 MMBtu/hr | 2018-10-01 | Same as normal operation BACT requirements. | Maximum opacity 5% | Firing pipeline quality natural gas and good combustion practices. Specify if firing a different fuel. | No data | Burners with the best NOx performance given the burner configuration and gaseous fuel used. Specify the proposed emission rate (performance is an annual average) and provide justification if NOx>0.01 lb/MMBtu. | Maximum 0.6% sulfur content any liquid fuel or 5 grains for pipeline quality sweet natural gas. Provide details. | 50 ppmv corrected to 3% O2 | No data | No data | No data | No data | No data
Hopper | 2018-10-01 | Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Hoppers shall be equipped with a filter control device such as a baghouse, cartridge filter system or bin vent filter. Outlet grain loading of ≤ 0.002 grains/dry standard cubic foot or an efficiency of at least 99.9% | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Incinerator: air curtain | 2018-10-01 | Maintenance activities will be authorized either by PBR or De Minimis. Combustion emission factors used when developing the normal operation emission rates include enough conservatism to account for incidental increases that could occur during startup and shutdown. | Good combustion practices and work practices, operational limitations. | Good combustion practices and work practices, operational limitations. | No data | Good combustion practices and work practices, operational limitations. | Good combustion practices and work practices, operational limitations. | Good combustion practices and work practices, operational limitations. | No data | No data | No data | No data | No data
Incinerator: animal carcass | 2018-10-01 | Operating the facility the facility in accordance with best management practices and good air pollution control practices. | Secondary chamber temperature of at least 1600⁰F. Gas residence time greater than 0.5 seconds. | Secondary chamber temperature of at least 1600⁰F. Gas residence time greater than 0.5 seconds. | No data | Secondary chamber temperature of at least 1600⁰F. Gas residence time greater than 0.5 seconds. | Secondary chamber temperature of at least 1600⁰F. Gas residence time greater than 0.5 seconds. | Secondary chamber temperature of at least 1600⁰F. Gas residence time greater than 0.5 seconds. | No data | No data | No data | No data | No data
Incinerator: hazardous waste | 2018-10-01 | Waste may not be added after startup until secondary chamber reaches 1800 degrees. Shutdown may not commence until all waste in the primary chamber is consumed. | Must meet the standards for 40 CFR Part 63-Subpart EEE. | Must meet the standards for 40 CFR Part 63-Subpart EEE. | No data | Must meet the standards for 40 CFR Part 63-Subpart EEE. | Must meet the standards for 40 CFR Part 63-Subpart EEE. | Must meet the standards for 40 CFR Part 63-Subpart EEE. | No data | No data | Must meet the standards for 40 CFR Part 63-Subpart EEE. | Must meet the standards for 40 CFR Part 63-Subpart EEE. | Must meet the standards for 40 CFR Part 63-Subpart EEE.
Incinerator: medical waste | 2018-10-01 | Waste may not be added after startup until secondary chamber reaches 1800 degrees. Shutdown may not commence until all waste in the primary chamber is consumed. | Specify technique: 1. dry scrubber: 0.015 gr/dscf at 7% O2 (front and back halves) 2. wet scrubber: 0.020 gr/dscf at 7% O2 (front and back halves) Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | 20-50 ppmvd at 7% O2 or 80% reduction, typically achieved with a dry or wet scrubber. Specify technique and numeric value. Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | 50 ppmvd at 7% O2. Specify technique. Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | Specify technique: 1. dry scrubber: 97% reduction by weight 2. wet scrubber: 99% reduction by weight Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail.
Incinerator: municipal solid waste | 2018-10-01 | Waste may not be added after startup until secondary chamber reaches 1800 degrees. Shutdown may not commence until all waste in the primary chamber is consumed. | manufacturer's specifications, and operated as necessary to maintain the minimum | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | 30 ppmvd at 7% O2 or 80% reduction, typically achieved with a dry or wet scrubber. Specify technique. Secondary chamber temperature of at least 1800˚ F. Minimum of 1 second retention time. | 50 ppmvd at 7% O2. Specify technique. Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail. | No data | 25 ppmvd at 7% O2 or 95% reduction, typically achieved with a dry or wet scrubber. Specify technique. Secondary chamber temperature of at least 1800˚ F. Provide detail. Minimum of 1 second retention time. Provide detail.
Kiln: cement | 2018-10-01 | Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. ESP shall be brought up to manufacturer's suggested temperature and maintained at that temperature for a duration of time specified by manufacturer before being placed into service. Cyclones shall be maintained according to manufacturer's specifications. | Fabric filter, ESP, wet scrubber, or cyclone. Specify technique. For Portland Cement: PM shall be limited to 0.02 lb/ton clinker . For Lime: 0.10 lb/tons stone feed (tsf) Must meet the limits of 40 CFR 63 Subpart LLL. | Good combustion practices or oxidizers. Total Hydrocarbons limited to 24 ppmvd at 7% O2. | No data | Dry low NOX combustors, NSCR, or water/steam injection. Specify technique. These controls will limit NOx to 1.5 lb/ton clinker on a 30-day rolling average. Must meet the limits of 40 CFR 60 Subpart F. | Firing low sulfur fuel and/or scrubber. Specify technique. SO2 shall be limited to 0.4 lb/ton clinker on a 30-day rolling average. Must meet the limits of 40 CFR 60 Subpart F. | Good combustion practices or oxidation catalyst. Specify technique. | Control of ammonia injection system to minimize ammonia slip. | Firing low sulfur fuel and/or scrubber. Specify technique. | Firing low sulfur fuel and/or scrubber. Specify technique. | Activated carbon injection and/or sorbent injection. Specify technique. Hg shall be limited to 21 lb/MM tons clinker. Must meet the limits of 40 CFR 63 Subpart LLL. | Limited to 3 ppmvd at 7% O2. Must meet the limits of 40 CFR 63 Subpart LLL.
Material handling: conveyor | 2018-10-01 | Best management practices (conducting system maintenance in a manner which minimizes emissions) employed during handling system maintenance. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Coal handling: 90% reduction, typically enclosed (50-90% reduction); chemical sprays (80-90% reduction; or full enclosure (90+%). Specify technique. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Material handling: drop point | 2018-10-01 | Best management practices (conducting system maintenance in a manner which minimizes emissions) employed during handling system maintenance. No bypassing of controls. Suction shroud should be in good repair with minimum flow rate. | 99% reduction or 0.01 gr/dscf, suction shroud, minimum 4000 acfm. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Material handling: product transfer/dump | 2018-10-01 | Best management practices (conducting system maintenance in a manner which minimizes emissions) employed during handling system maintenance. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | All: 70% reduction, typically achieved with water sprays. Wet material (1.5% moisture minimum) 50% reduction; enclosure methods, dependent upon ratio of openings in enclosure 50-90%; fabric filter baghouses require 0.1 gr/dscf (99% reduction). Specify technique. Specify type. 1. Pneumatic: 99% reduction, outlet grain loading ≤ 0.01 gr/dscf. Typically achieved with a baghouse. Specify technique. 2. Mechanical: Enclosed conveying or equivalent. Specify. Coal handling: 85% reduction, typically achieved with foam and/or surfactant | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Material handling: receiving | 2018-10-01 | Best management practices (conducting system maintenance in a manner which minimizes emissions) employed during handling system maintenance. No bypassing of controls. Suction shroud should be in good repair with minimum flow rate. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | Barge: Grain elevator: 90% reduction, typically achieved by choke feeding at gravity receiving pits. Specify technique. Gravity: 90% reduction. Typically achieved by choke feeding. Specify technique. Pneumatic: 99% reduction, outlet grain loading ≤ 0.01 gr/dscf. Typically achieved with a baghouse. Specify technique. Rail: Coal: 90% reduction, typically foam sprays and enclosures | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Material handling: screen | 2018-10-01 | Best management practices (conducting system maintenance in a manner which minimizes emissions) employed during handling system maintenance. No bypassing of controls. | Coal: 90% reduction, typically enclosed or partial enclosure and water sprays. Specify technique. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
MSS activities | 2018-10-01 | Use of good air pollution control practices and safe operating practices. Limiting the frequency and duration of activities. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Process vent | 2018-10-01 | Same as normal operation BACT requirements. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | 99% reduction or outlet grain loading of 0.01 gr/dscf, typically achieved with fabric filters. Specify technique. | Non-halogenated VOCs: flare, any oxidizer, adsorber, absorber/scrubber, etc. Specify technique. Must meet that control device's approved efficiency. Halogenated VOC: Thermal oxidation followed by absorber/scrubber or carbon adsorption. Specify technique. Must meet that control device's approved efficiency. | No data | No data | No data | No data | No data | No data | No data | No data | No data
Roads | 2018-10-01 | Best management practices (roads are watered, traffic and speed are reduced) employed during maintenance, no additional controls required for startup and shutdown operations beyond normal operation BACT requirements. No bypassing of controls. | All: No visible emissions shall leave the property. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA TM 22 or equivalent. Coal plant: 70% reduction, typically achieved with water sprays. Specify technique. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Storage: silo | 2018-10-01 | Best management practices (minimizing spills, cleaning spills promptly, and using low volatility cleaning materials) during maintenance. No additional controls required for startup and shutdown operations if normally required controls are employed. No bypassing of controls. Fabric filters should be in good repair with an acceptable pressure drop prior to the start of operation. Removal of spent filters in such a manner to minimize PM emissions and placing the spent filters in sealable bags or other sealable containers prior to removal from the site. Bags or containers shall be kept closed at all times except when adding spent filters. | 99% reduction or outlet grain loading of 0.01 gr/dscf (combined front and back half), typically achieved with fabric filters. Specify if different. Maximum opacity of 5%. (1% from asphalt mineral handling.) No visible emissions shall leave the property from the silo loading. Visible emissions shall be determined by a standard of no visible emissions exceeding 30 seconds in duration in any six-minute period as determined using EPA TM 22 or equivalent. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Storage: stockpile | 2018-10-01 | No downtime since water sprays at transfer points and on stockpiles should be functioning prior to the start of operation. | All: 70% reduction, typically achieved with water spray systems. Specify if different. | No data | No data | No data | No data | No data | No data | No data | No data | No data | No data
Turbine: combined cycle, natural gas | 2018-10-01 | Minimizing the duration of MSS activities and minimizing the amount of time the turbine is outside the performance mode where the controls can be used. Operating the facility in accordance with best management practices and good air pollution control practices. | Good combustion practices. Fuel limited to firing pipeline quality natural gas. | 2 ppmvd at 15% O2 if no duct burner, 4 ppmvd with duct burner. Achieved through good combustion practices. | No data | 2.0 ppmvd at 15% O2, 24-hour average, typically achieved with dry low NOX burner, water/steam injection, limiting fuel consumption, or SCR. Specify numeric value and proposed technique. | Good combustion practices. Fuel limited to firing pipeline quality natural gas (low sulfur fuel). Sulfur content of fuel will not exceed 5 grains per 100 scf on an hourly basis and 1 gr/100 scf on an annual basis. | 2-4 ppmvd at 15% O2, typically achieved with good combustion practices and/or oxidation catalyst. Specify numeric value and control technique. A detailed analysis is required if >4 ppmvd is proposed. | 7-10 ppmvd at 15% O, achieved by controlling the ammonia injection system to minimize ammonia slip | No data | Good combustion practices. Fuel limited to firing pipeline quality natural gas (low sulfur fuel). Sulfur content of fuel will not exceed 5 grains per 100 scf on an hourly basis and 1 gr/100 scf on an annual basis. | No data | No data
Turbine: simple cycle, natural gas | 2018-10-01 | Minimizing the duration of MSS activities and operating the facility in accordance with best management practices and good air pollution control practices. | Good combustion practices. Fuel limited to firing pipeline quality natural gas. | 2 ppmvd at 15% O2 achieved through good combustion practices. | No data | 5.0 to 9.0 ppmvd at 15% O2, typically achieved with dry low NOX burner, water/steam injection, limiting fuel consumption, or SCR. Specify numeric value and proposed technique. | Good combustion practices. Fuel limited to firing pipeline quality natural gas (low sulfur fuel). Sulfur content of fuel will not exceed 2 to 5 grains per 100 scf on an hourly basis and 0.5 to 1 gr/100 scf on an annual basis. | 9-25 ppmvd at 15% O2, typically achieved with good combustion practices and/or oxidation catalyst. Specify numeric value and control technique. A detailed analysis is required if >9 ppmvd is proposed. | 7-10 ppmvd at 15% O, achieved by controlling the ammonia injection system to minimize ammonia slip | No data | Good combustion practices. Fuel limited to firing pipeline quality natural gas (low sulfur fuel). Sulfur content of fuel will not exceed 5 grains per 100 scf on an hourly basis and 1 gr/100 scf on an annual basis. | No data | No data
End of worksheet