## Analytical Methods
List of Analytical Methods (LAM) for Monitoring Chloramines
You must document the methods and laboratories on this List of Analytical Methods (LAM).
Analyte: | The chemical or value that you are analyzing.
Analytical Method: | Fill in the method that you use to meausre for each analyte. For example, you can insert a standard method (ex: Standard Method Cl-4500D) or the make and model of the analyzer (Hach SL 1000).
Instrument Name: | Document the make and model of the instrument you are using to measure the analyte.
Accuracy: | Report the number of decimal places to which you can accurately report the value for each analyte. For a list of analytical requirements, please see §290.110(d).
Calibration Frequency and Method: | Report the frequency and method with which you calibrate or verify the accuracy of your equipment.
NAP Required Parameters
Analyte | Analytical Method | Instrument Name | Accuracy |  | Calibration Frequency | Calibration Method
Monochloramine |  |  |  | mg/L
Free Ammonia (as nitrogen) |  |  |  | mg/L
Nitrite (as nitrogen) |  |  |  | mg/L
Nitrate (as nitrogen) |  |  |  | mg/L
Other NAP Indicators
Chlorite |  |  |  | mg/L
pH |  |  |  | pH unit
Temperature |  |  |  | C or F
Alkalinity |  |  |  | mg/L
TDS |  |  |  | mg/L
Heterotrophic plate count bacteria
Microbial DNA
Other

## NAP Template
PWS Name: |  |  |  | Nitrification Action Plan
PWS ID: |  |  | Operator in Responsible Charge, Printed Name |  | Date
Operator in Responsible Charge, Signature
Nitrification Action Plan Template
Chloramine-Effectiveness Sample Suite
Site | Chemical | Goal | Yellow Flag |  | Red Flag
|  |  | Trigger | Actions | Trigger | Actions
Entry Point | Total / Mono
Free ammonia
Average Water Age | Total / Mono
Free ammonia
High Water Age | Total / Mono
Free ammonia
Nitrite/Nitrate
Site | Chemical | Baseline | Yellow Flag |  | Red Flag
|  |  | Trigger | Actions | Trigger | Actions
Entry Point | Nitrite
EP#___ | Nitrate
Source water(s) | Nitrite
Nitrate
Blended water | Nitrite
Nitrate
Note: The NAP must include a map showing the NAP sample sites, entry points, sources, storage, treatment, and any other pertinent locations.
This template must be modified to show all entry points and sources at the system. The EP# is shown at dww2.tceq.texas.gov/DWW/
Analytical methods must meet minimum accuracy and be documented on the Laboratory Approval Form (TCEQ Form #10450) in the Monitoring Plan.
Samples must be analyzed in the range of the instrument. If needed, dilutions must be done for samples that are out of range.
Note on C2: Insert the name of your public water system (PWS)
Note on C3: Insert your PWS's 7-digit identification number. You can look up PWS ID's by name at http://dww2.tceq.texas.gov/DWW/
Note on B7: We refer to: u Total chlorine, u Monochloramine, and u Free ammonia as the 'chloramine-effectiveness' suite of chemicals.
Note on E8: A 'Yellow Flag' is when the water is slightly off-spec.
Note on G8: A "Red Flag" occurs when the water is far from the desired condition.
Note on E9: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on F9: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on G9: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on H9: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on B10: All entry points must be included in the NAP. Add additional rows to take into account additional entry points.
Note on C10: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on D10: For entry points near treatment plants, the goal is set based on how high the residual must be to make sure a residual gets all the way through the system. For purchased water entry points, the baseline is the level that is provided by the wholesaler.
Note on C11: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on D11: For treated water entry points, the free available ammonia (as nitrogen) should be as close to zero as possible coming out of a treatment plant. For purchased-water entry points the baseline is whatever the wholesaler normally provides.
Note on B12: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on C12: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on D12: At average water age, the goal/baseline is the level that is acceptable and will allow a chloramine residual to last to the ends of the system.
Note on C13: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on D13: Free available ammonia (as nitrogen) will be released through the normal degradation of chloramines. The "Average Water Age" site goal/baseline should be higher than the "Entry Point" goal.
Note on B14: "Far reaches" sites would be those where it is most difficult to maintain a residual when nitrification is NOT occurring. For example, dead-end mains. If multiple sites are monitored, add lines to the table.
Note on C14: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on D14: The far reaches goal for total chlorine/monochloramine should be over the minimum required total chlorine residual of 0.5 mg/L to provide a safety factor.
Note on C15: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on D15: The "High Water Age" free ammonia goal can be higher than the "Average Water Age" site goal or the "Entry Point" goal because free available ammonia is a product of chloramimne degradation.
Note on E17: A 'Yellow Flag' is when the water is slightly off-spec.
Note on G17: A "Red Flag" occurs when the water is far from the desired condition.
Note on E18: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on F18: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on G18: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on H18: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on B19: All entry points must be included in the NAP. Add more rows for additional entry points.
Note on C19: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on D19: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B20: Verify your EP# on TCEQ's Drinking Water Watch at dww2.tceq.texas.gov/DWW/
Note on C20: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on D20: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B21: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on C21: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on D21: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on C22: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on D22: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B23: If two sources with different nitrite, nitrate, or free ammonia concentrations are blended at varying ratios--like when wells come on at different times--it can hurt the performance of chloramination. Therefore, the concentration in the blended water must be measured.
Note on C23: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on D23: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on C24: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on D24: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.

## Summary
Nitrification Action Plan (NAP)—Summary
The Texas Commission on Environmental Quality (TCEQ) has information about nitrification on our web site at: www.tceq.texas.gov/drinkingwater/disinfection/nitrification.html
The TCEQ's data for Texas public water systems (PWSs) is available at: dww2.tceq.texas.gov/DWW/
This summary is intended to describe and supplement the rule requirements of Title 30, Texas Administrative Code (30 TAC) Chapter 290. In the event of any unintended discrepancy between the rule and this guidance, the rule language shall apply.
Purpose of NAP: The purpose of a Nitrification Action Plan (NAP) is to ensure that chloramine disinfection is successful by preventing and/or responding to nitrification.
NAP Sampling: The rule gives the minimum requirements. It may be necessary for PWSs to perform additional sampling to characterize the adequacy of disinfection in their distribution system.
Critical Control Conditions for Chloramination
Total Chlorine | l Total chlorine is the sum of all active chlorine species. It is the regulated level. l The minimum allowable total chlorine residual is 0.5 mg/L throughout the distribution. l The maximum residual disinfectant level (MRDL) for total chlorine is 4.0 mg/L based on the running annual average (RAA) of all samples collected in distribution. Maintaining a residual over the 4.0 mg/L at entry points is not a violation in and of itself. l The minimum and maximum residuals in distribution are reported on the Disinfectant Level Quarterly Operating Report (DLQOR) and the Surface Water Monthly Operating Report (SWMOR).
Mono-chloramine | l Monochloramine is the disinfecting member of the chloramine family. l Ideally, all of the total chlorine will be present as monochloramine. l Keeping track of the ratio of monochloramine to total chlorine can help alert you to possible nitrification.
Free Ammonia | l Free ammonia reacts with free chlorine to make monochloramine and other chloramines. Then, as the monochloramine decays, free ammonia is released. l Free ammonia and total ammonia may be present in source water.
Nitrite | l Nitrite is formed by ammonia-oxidizing bacteria which 'eat' ammonia. l Nitrite may be present in source water. l Nitrite has a health-based maximum contaminant level (MCL) of 1 mg/L at entry points, but is not regulated at distribution system sample sites. However, it is still a public health concern when it is over the MCL.
Nitrate | l Nitrate is formed by nitrite-oxidizing bacteria which 'eat' nitrite. l Nitrate is often present in source water, especially groundwater. l Nitrate has a MCL of 10 mg/L at entry points, but is not regulated at distribution system sample sites. However, it is still a public health concern when over the MCL.
Other process management parameters
Free chlorine | l You are not required to measure free chlorine, except during a temporary conversion to free chlorine performed as a preventive or corrective action.
pH | l A decrease in pH can indicate nitrification. Therefore, pH measurement is recommended at systems with low alkalinity. l PWSs that use pH elevation for corrosion or nitrification control should also monitor pH in the distribution system. l Some PWSs are required to measure pH as part of the Lead and Copper Rule requirements for WQP (water quality parameter) testing.
HPC | l HPC means 'heterotrophic plate count' bacteria. l HPC can be a useful tool to measure the concentration of a broad range of bacteria. An increase in HPC can indicate nitrification. l PWSs are not required to measure HPC.
Other indicators | Nitrification/denitrification indicators used in wastewater treatment, such as dissolved oxygen, alkalinity, oxidation-reduction potential may be useful for drinking water in future, but need further research.
NAP Sample Sites
l Sample sites must represent the distribution system and all entry points. l In addition to routine NAP sample sites, additional locations will need to be sampled when taking action to identify the area where nitrification is happening.
Storage tanks | l Storage facilities can increase water age. Consider the impact of storage when determining sample sites.
Sample Sites Before and After Chemical Injection
Source(s) | Ground-water | l All wells are required to have pre-disinfection sample taps representing the raw water. l If only one well and one entry point are present, entry point nitrite/nitrate sample results may be used to represent source water nitrite/nitrate levels. l If more than one well feeds one entry point, nitrite, nitrate, and free ammonia sampling must be performed at each well.
| Surface water (and GUI) | l Surface water systems must monitor raw water for nitrite, nitrate, and free ammonia representing each raw water intake. l GUI is groundwater under the direct influence of surface water. GUI must meet the requirements for surface water.
| Purchased water | l For purchased water, the source sample site is usually the entry point sample site. l Systems that purchase and redistribute potable water must measure total chlorine, monochloramine, free ammonia, nitrite, and nitrate immediately after the water enters their system.
Entry Point(s) | l Entry points are defined as a point where treated water enters the distribution system. All entry points are required to have a representative sample tap. l Entry points are numbered. You can verify this number on TCEQ's web site: 'Drinking Water Watch' at dww2.tceq.texas.gov/DWW/ l For the purposes of a NAP, entry point sampling is the same regardless of the water source type.
Sample Sites Before and After Chemical Injection
l Sampling is required to make sure that the correct chlorine-to-ammonia (Cl:N) ratio exists. The Cl:N ratio is calculated from the mass of free chlorine to the mass of free-ammonia-nitrogen. The desired range of Cl:N is ~ 4:1 to 5:1. The range from 5:1 to 8:1 is undesirable because of di- and trichloramine formation; above 8:1 all nitrogen is lost and free chlorine is present. l PWS staff should become familiar with breakpoint chemistry. l Good mixing during treatment is very important. Poor mixing can cause ineffective disinfection.
Order of addition | l When chlorine is injected upstream of any other disinfectant, the ammonia injection point must be downstream of the chlorine injection point. l When chlorine and ammonia are added to distribution water that has a chloramine residual, ammonia should be added first. l When chlorine and ammonia are added to distribution water that has a free chlorine residual, chlorine should be added first.
Before chemical addition | l Sampling must be performed upstream of the chlorine or ammonia chemical injection point, whichever is furthest upstream. l If free ammonia is present in the source, raw water sampling should be performed weekly. l If the source is purchased potable water--total chlorine, monochloramine, and free ammonia must be monitored at least weekly and dosing should consider influent levels.
During treatment | l Chlorine must be injected before ammonia. l Sampling must be performed downstream of all the chlorine and ammonia chemical injection points.
Booster disinfection | l The free ammonia (as nitrogen) and monochloramine residuals must all be monitored if the treatment occurs in the distribution system. The monitoring must occur at the same time as a total chlorine compliance sample. l If potable water is redisinfected, the disinfectant residual must not fall below the minimum anywhere, including right before treatment. l The residual of the chemical injected upstream should be determined to properly dose the downstream chemical.
NAP Sample Sites, continued
Distribution System Sample Sites
l Routine coliform and/or disinfectant residual sites may be used for NAP sample sites. l Sites must represent the distribution system and represent average and high water age. Small systems may be adequately represented with two or three sites; medium and large systems will need to specify more sites to adequately detect and prevent potential nitrification. The rule does not specify the exact number of sample sites because of the diversity among PWSs. l It is recommended that 'critical control points' be selected. In distribution, these may be at interconnections between major mains, storage facilities, pump stations, and interconnections with other PWSs.
Average water age | l As a first estimate, average water age can be estimated from historical data as locations with average total chlorine residual. l Enough average water age sites must be selected to represent multiple pressure planes.
High water age | l High water age may occur at the far reaches of the distribution system, in under-used areas, or as a result of storage. l Sites should represent all pressure planes.
NAP Sample Frequency
Sample Frequency: The rule lists the minimum sampling requirements. It may be necessary for PWSs to perform additional sampling to characterize their distribution system.
| At or after all Entry Point(s) |  | In the distribution system |  | Before and after any chlorine or ammonia injection points
Total Chlorine | Weekly. |  | Daily/weekly.a |  | Weekly and before and after adjusting the chlorine or ammonia feed rate.
Mono-chloramine |  |  | At least weekly.b
Free Ammonia
Nitrite and Nitrate | Monthly for six (6) months, then quarterly. |  | At least quarterly and in response to action triggers. |  | Routine sampling not required.
a. Total chlorine must be collected weekly or daily, based on the system size, in accordance with §290.110.
b. When collecting a routine sample such as a bacteriological or routine disinfectant residual sample.
Methods
l The methods used must be accurate enough to measure changes that can indicate nitrification. l You must document the methods and laboratories for total chlorine on your PWS Laboratory Approval Form (Form # TCEQ-10450) attached to your Monitoring Plan. The methods and/or laboratories used for monochloramine, free ammonia, nitrite and nitrate must be documented in your NAP.
Required accuracy:
Total Chlorine | 0.1 mg/L | l Total chlorine must be analyzed in the field. l Amperometric titration, DPD ferrous titration, or DPD colorimetric are the required methods. l Check the range of your kit. If a sample is outside range, dilute and reanalyze.
Mono-chloramine | 0.15 mg/L | l Monochloramine must be analyzed in the field. l Any method approved for the drinking water matrix is acceptable.
Free Ammonia (as nitrogen) | 0.1 mg/L | l Free ammonia must be analyzed in the field. l Ammonia is measured as 'free available ammonia as nitrogen.' l Check the range of your kit. The most common one pegs out at 0.55 mg/L®samples over that level must be diluted and re-analyzed. l Any method approved for the drinking water matrix is acceptable.
Nitrite (as nitrogen) | 0.01 mg/L | l Nitrite and nitrate may be analyzed in the field and/or in an accredited or approved lab. l If samples are analyzed at an outside approved lab, keep a copy of that lab's accreditation documents with your NAP.
Nitrate (as nitrogen) | 0.1 mg/L
Goals and Baselines
l Goals and baselines are the normal, good levels at each point in the distribution system. 'Goals' are set for total chlorine, monochloramine, and free ammonia to make sure that disinfection is maintained correctly. 'Baselines' are set for nitrite and nitrate, because they come from source water, and are less under a system's control. l Initial results and historical data are used to set goals and baselines. l Ongoing, routine sampling is used to detect potential nitrification and take appropriate action.
Total chlorine & Mono- chloramine Goals | l Total chlorine and monochloramine should always be about the same, so their goals can be set at the same value. l The entry point goal should be high enough so that the maximum water age site can achieve its goal over the minimum of 0.5 mg/L plus a safety factor.
Free ammonia Goal | l Ideally, water at entry points just after treatment would have zero free ammonia residual because free ammonia is 'food' for the nitrifying bacteria. l Having a trace of free ammonia shows that the water is in the monochloramine zone. l Free ammonia naturally increases with time. The free ammonia goals in average and high water age locations should represent good, normal operating conditions.
Nitrite & nitrate Baselines | l The nitrite and nitrate baselines are the concentrations in the source water. l The nitrite and nitrate in the distribution system should always be the same as the source water. l The only thing that can change them is either nitrification, backflow or cross connection, or source water changes.
Triggers: Yellow Flag Alerts, Red Flag Alarms
Yellow flag 'alert' triggers: Yellow flag levels are somewhat out of the norm, indicating that nitrification may have started. Some action to get back to normal is needed--but it is probably a routine type of action like flushing.
Red flag 'alarm' triggers: Red flag levels happen when it becomes difficult to maintain a compliant total chlorine residual, and there is a strong possibility that nitrification is the culprit. If routine actions don't get the system back to normal, more intense action will be needed.
Total chlorine | l Total chlorine is the regulated value, so most systems have more data for total chlorine than any other constituent. Therefore, PWSs should have at least a year of historical weekly or daily data to use for setting triggers. l If a nitrification event has occurred, the exact levels where nitrification took place can be used. Otherwise, yellow and red trigger levels should be estimated.
Mono-chloramine | l Ideally, 100% of the total chlorine should be present as monochloramine. l Systems may have characteristic ratios of monochloramine-to-total, for example: 80% or 90%.
Free ammonia | l Ammonia will decrease during nitrification. If ammonia is not detected, nitrification is the likely cause.
Nitrite | l Nitrite may increase or decrease during nitrification. Therefore, any significant deviation of the nitrite level could indicate nitrification. l During the initial stages of nitrification, nitrite will increase; as nitrification progresses, nitrite will drop as it is converted to nitrate.
Nitrate | l Nitrate increases when nitrification is very bad. l The only possible reasons to for nitrate to increase are (1) Nitrification, (2) Cross-connection, backflow, or backsiphonage of sewage or fertilizer, or (3) Source water contamination. Any of these is a major issue.
Actions
Note: The TCEQ provides these examples of actions for guidance only. Each PWS that uses chloramines must select actions appropriate to its unique circumstances.
l Normal operations: When disinfection is going well, preventive actions are used to keep it going that way. This is the 'green zone.'
l Yellow flag 'alert' actions: When your nitrification indicators hit yellow flag levels, some action is needed to get back to normal. Often these corrective actions are similar to the preventive actions, like sampling and flushing.
l Red flag 'alarm' actions: When the total chlorine residual drops to low levels, nitrification may have progressed far enough that more extreme measures are needed to get back on track. If not, there may be another problem like cross-connection or treatment failure that needs attention.
Routine Preventive Actions / |  |  |  | Yellow Flag Alert Corrective Actions
Sample verification | l Before making a decision on what further action to take, it's a good idea to double-check the first measurement. l It is a good idea to double-check accuracy routinely, to document the variability of the analysis method.
Nitrite/ nitrate sampling | l Nitrite is a key indicator of nitrification. If chloramine-effectiveness measurements are off-spec, nitrite and nitrate sampling is necessary to determine if nitrification is happening. l Although the rule only requires 6 samples to set baselines, more nitrite and nitrate data will improve your ability to respond to potential nitrification.
Determine affected area | l Nitrification is a biological process, so it can 'bloom' in one portion of the distribution system while other areas remain okay. Determining what area is affected will allow a targeted response to effectively stop the nitrification.
Flushing | l Flushing can bring fresh water with a strong chloramine residual to a location where disinfectant levels are decreasing. However, it is only a short-term solution because of the conservation, economic, and customer relations impacts. l Every PWS is required to flush every dead-end main (DEM) every month.
Uni- directional flushing | ll Unidirectional flushing (UDF) is a way of organizing flushing to achieve a velocity of 5 feet-per-second (FPS) in the pipe. At 5 fps, suspended sediment is effectively removed. UDF can be used to target a problem area.
Pigging | ll Pigging is the process where a cylindrical 'pig' is forced through a water main with hydraulic pressure, forcing sediment to be scraped off the walls then removed at a flush point. Pigging is best used where the system has been designed with entry and exit points for the pig. Pigging is not considered practical for old, weak pipe.
Storage tank operation | ll Storage is often a cause of increased water age. Optimizing storage tank operations means selecting the best operating levels where there is enough water for use, but not so much that it sits in the tank decaying too long.
Free chlorine conversion | ll Free chlorine conversion is often called a 'burn,' 'shock,' or 'refresh.' When free chlorine is present, it starves nitrifying bacteria. Although a free chlorine conversion is sometimes thought of as an extreme measure, there are numerous PWSs that perform routine, annual free chlorine conversion as a preventive measure. ll E-mail the TCEQ at DBP@tceq.texas.gov 30 days before doing a free chlorine conversion.
Red Flag Alarm Corrective Actions
Routine actions | lll The same actions (listed above) that are used for preventive maintenance and yellow-flag correction may be a part of the corrective actions used for red-flag actions.
Free chlorine conversion | l Free chlorine conversion is often used to respond to nitrification. Contact TCEQ at 512-239-4691 or DBP@tceq.texas.gov to discuss scheduling a free chlorine conversion.
Actions, continued
Seek professional help for engineered modifications
TCEQ's Plan and Technical Review Section can assist you with questions related to the process of getting approval for engineered solutions at 512-239-4691 or on the web at: www.tceq.texas.gov/drinkingwater/planrev.html
Looping mains | l If a PWS identifies nitrification due to dead-end mains (DEMs), it may be appropriate to perform infrastructure replacement in the problem area to manage water age. ll Every PWS is required to have a program to minimize stagnation of water due to DEMs.
Tank changes | l Tanks can be a source of major water age. In some cases, a PWS may choose to completely eliminate tanks or replace larger tanks with smaller ones. ll Some PWSs have found mixing to be helpful in eliminating chloramine residual loss due to tank stratification. ll Tanks must always have a compliant disinfectant residual.
Booster disinfection | ll If the size and shape of a distribution system are very challenging, the addition of booster chloramination may be appropriate. Usually, both chlorine and ammonia injection should be at the booster station. However, if the water upstream of the booster contains free ammonia, it is possible to inject chlorine to tie up that free ammonia and form monochloramines. In that case, ammonia injection might not be needed.
pH adjustment | ll Monochloramine is more stable at a higher pH. Nitrifying organisms grow more rapidly at pH 7.5 than at pH 8. For these reasons, a PWS may choose to adjust pH. If pH adjustment is used, the impact on corrosion control should be considered.
Free chlorine & aeration | l Some groundwater systems with high total organic carbon have used free chlorination followed by aeration to volatilize chloroform to make it possible to meet disinfection byproduct regulations with a free chlorine distribution system residual.
Chlorite feed | l Research shows that the presence of chlorite may slow or stop nitrification from developing. It will not necessarily work to stop nitrification that has already started. Chlorite is a regulated disinfection byproduct of chlorine dioxide. A system considering chlorite feed should be prepared to perform chlorite sampling in distribution.
Other solutions? | Research continues on nitrification. Some new methods may be snake oil, but others may turn out to be successful. Use professional development opportunities to learn about new technology.
This is a template for a starting a NAP. It is provided for guidance; a PWS must develop a site-specific NAP and map.
Example: Nitrification Action Plan Template
Chloramine-Effectiveness Sample Suite
Site | Chemical | Goal | Yellow Flag |  |  | Red Flag
|  |  | Trigger | Actions |  | Trigger | Actions
Entry Point | Total / Mono | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Ammonia | ___ mg/L | ___ mg/L |  |  | ___ mg/L
Average water age | Total / Mono | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Ammonia | ___ mg/L | ___ mg/L |  |  | ___ mg/L
High water age | Total / Mono | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Ammonia | ___ mg/L | ___ mg/L |  |  | ___ mg/L
Nitrite/Nitrate
Site | Chemical | Baseline | Yellow Flag |  |  | Red Flag
|  |  | Trigger | Actions |  | Trigger | Actions
Entry Point | Nitrite | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Nitrate | ___ mg/L | ___ mg/L |  |  | ___ mg/L
Source water(s) | Nitrite | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Nitrate | ___ mg/L | ___ mg/L |  |  | ___ mg/L
Blended water | Nitrite | ___ mg/L | ___ mg/L |  |  | ___ mg/L
| Nitrate | ___ mg/L | ___ mg/L |  |  | ___ mg/L
Note on A26: Different sources will have different amounts of naturally-occurring nitrite, nitrate, and free ammonia. Purchased water systems may also have variable amounts of total chlorine and monochloramines. Therefore, PWSs need to know the contribution from each source.
Note on B26: Groundwater may contain naturally occurring nitrite, nitrate, and free ammonia. You need to account for this in treatment calculations.
Note on B27: Surface water is more highly regulated than other sources. Make sure that all surface water requirements are met, in addition to these NAP requirements.
Note on A40: As a first estimate, select sites that normally have average total chlorine residual as your 'average water age' sites.
Note on A41: High water age sites might be in the far reaches, at dead-end mains or after large storage tanks.
Note on A108: We refer to: u Total chlorine, u Monochloramine, and u Free ammonia as the 'chloramine-effectiveness' suite of chemicals.
Note on D109: A 'Yellow Flag' is when the water is slightly off-spec.
Note on G109: A "Red Flag" occurs when the water is far from the desired condition.
Note on D110: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on E110: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on G110: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on H110: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on A111: All entry points must be included in the NAP. Add additional rows to take into account additional entry points.
Note on B111: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on B112: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on A113: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on B113: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on B114: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on A115: "Far reaches" sites would be those where it is most difficult to maintain a residual when nitrification is NOT occurring. For example, dead-end mains. If multiple sites are monitored, add lines to the table.
Note on B115: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on B116: If the colorimeter flashes "0.55" you need to do a dilution because the ammonia concentration is higher than the range of the instrument.
Note on D118: A 'Yellow Flag' is when the water is slightly off-spec.
Note on G118: A "Red Flag" occurs when the water is far from the desired condition.
Note on D119: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on E119: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on G119: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on H119: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on A120: All entry points must be included in the NAP. Add additional rows to take into account additional entry points.
Note on B120: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on B121: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on A122: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on B122: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on B123: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on A124: If two sources with different nitrite, nitrate, or free ammonia concentrations are blended at varying ratios--like when wells come on at different times--it can hurt the performance of chloramination. Therefore, the concentration in the blended water must be measured.
Note on B124: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on B125: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.

## ExampleNAPtable
This is an example of a completed NAP. A PWS must determine their own site-specific sample points, goals, baselines, triggers, and actions.
Nitrification Action Plan Example
Chloramine-Effectiveness Sample Suite
Site | Chemical | Goal | Yellow Flag |  | Red Flag
|  |  | Trigger | Actions | Trigger | Actions
Entry Point | Total / Mono | 4.2 | 3.5 | 1) Verify results 2) Check and adjust dose ®Till levels return to normal | 3.0 | 1) Verify results 2) Adjust dose ®Till levels return to normal
| Free ammonia | 0.01 | 0.2 |  | 0.3
Average Water Age | Total / Mono | 2.0 | 1.5 | 1) Verify results 2) Measure nitrite and nitrate 3) Adjust dose 4) Identify affected area (check upstream and downstream) 5) Flush area 6) Flush dead ends ®Till levels return to normal | 1.0 | 1) Verify results 2) Measure nitrite and nitrate 3) Adjust dose 4) Identify affected area (check upstream and downstream) 5) Flush area 6) Flush dead ends 7) Convert to Free Chlorine ®Till levels return to normal
| Free ammonia | 0.3 | +/- 20% |  | +/- 50%
High Water Age | Total / Mono | 1.0 | 0.7 |  | 0.5
| Free ammonia | 0.5 | +/- 20% |  | +/- 50%
Nitrite/Nitrate
Site | Chemical | Baseline | Yellow Flag |  | Red Flag
|  |  | Trigger | Actions | Trigger | Actions
Entry Point | Nitrite | 0.025 | +/- 20% (<0.02 or >0.03) | 1) Verify results 2) Identify source changes IF confirmed-modify BL 3) Identify area, 4) Flush area ®Till levels return to normal | +/- 50% (<0.013 or >0.05) | 1) Verify results 2) Identify affected area 3) Flush 4) Perform free chlorine burn ®Till levels return to normal
| Nitrate | 1.5 | >1.7 |  | >2.0
Source water(s) | Nitrite | 0.025 | +/- 20% (<0.02 or >0.03) |  | +/- 50% (<0.013 or >0.05)
| Nitrate | 1.5 | >1.7 |  | >2.0
Blended water | Nitrite | 0.025 | +/- 20% (<0.02 or >0.03) |  | +/- 50% (<0.013 or >0.05)
| Nitrate | 1.5 | >1.7 |  | >2.0
Note: The NAP must include a map showing the NAP sample sites, entry points, sources, storage, treatment, and any other pertinent locations.
Note on A3: We refer to: u Total chlorine, u Monochloramine, and u Free ammonia as the 'chloramine-effectiveness' suite of chemicals.
Note on D4: A 'Yellow Flag' is when the water is slightly off-spec.
Note on F4: A "Red Flag" occurs when the water is far from the desired condition.
Note on D5: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on E5: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on F5: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on G5: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on A6: All entry points must be included in the NAP. Add additional rows to take into account additional entry points.
Note on B6: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on C6: For entry points near treatment plants, the goal is set based on how high the residual must be to make sure a residual gets all the way through the system. For purchased water entry points, the baseline is the level that is provided by the wholesaler.
Note on B7: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on C7: For treated water entry points, the free available ammonia (as nitrogen) should be as close to zero as possible coming out of a treatment plant. For purchased-water entry points the baseline is whatever the wholesaler normally provides.
Note on A8: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on B8: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on C8: At average water age, the goal/baseline is the level that is acceptable and will allow a chloramine residual to last to the ends of the system.
Note on B9: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on C9: Free available ammonia (as nitrogen) will be released through the normal degradation of chloramines. The "Average Water Age" site goal/baseline should be higher than the "Entry Point" goal.
Note on A10: High Water Age sites would be those where it is most difficult to maintain a residual when nitrification is NOT occurring. For example, dead-end mains. If multiple sites are monitored, add lines to the table.
Note on B10: Total chlorine and monochloramine should be almost the same. If they are not the same, it may indicate a problem.
Note on C10: The far reaches goal for total chlorine/monochloramine should be over the minimum required total chlorine residual of 0.5 mg/L to provide a safety factor.
Note on B11: Remember--many field kits only measure up to 0.5 mg/L for free available ammonia (as nitrogen). Dilutions must be performed for higher residual ammonia.
Note on C11: The "Far Reaches" goal should be higher than the "Average Water Age" site goal or the "Entry Point" goal because free available ammonia is a product of the degradation of chloramines.
Note on D13: A 'Yellow Flag' is when the water is slightly off-spec.
Note on F13: A "Red Flag" occurs when the water is far from the desired condition.
Note on D14: A 'Yellow Flag' trigger should describe water that is not exactly where you want it, but not too far off.
Note on E14: Actions to respond to a slight problem (Yellow Flag) are generally simple, routine actions like verifying the result and flushing.
Note on F14: A 'Red Flag' trigger should describe the conditions when the water is far from your desired conditions.
Note on G14: The 'Red Flag' actions may be more extreme than 'Yellow Flag' actions. For example, a free-chlorine conversion might be needed.
Note on A15: All entry points must be included in the NAP. Add additional rows to take into account additional entry points.
Note on B15: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on C15: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B16: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on C16: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on A17: Normally, average water age sites are any sites that fall between entry point and far reach sites. For large distribution systems, you may need to identify goals for more than one average site. In that case, add additional lines to the table.
Note on B17: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on C17: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B18: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on C18: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on A19: "Far reaches" sites would be those where it is most difficult to maintain a residual when nitrification is NOT occurring. For example, dead-end mains. If multiple sites are monitored, add lines to the table.
Note on B19: Nitrification will initially cause nitrite to increase as the AOB 'eat' the ammonia to form nitrite. Then, as the NOB 'eat' the nitrite to form nitrate, the nitrite can go down.
Note on C19: The nitrite baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.
Note on B20: If nitrification is allowed to persist, eventually all of the available nitrogen will be converted to nitrate.
Note on C20: The nitrate baseline is the average of normal results. If multiple sources are present, a baseline may need to be established for the different sources.

## ExampleData
Example of Normal Conditions Vs. Nitrification
Normal Conditions
Site ID | Address | Type | Date | Time | Calculated Flow Rate | Minutes Flushed | pH | Total Chlorine* | Mono-chloramine | Free Ammonia | Nitrite | Nitrate
[8 empty] | [mg/L] | [mg/L] | [mg/L] | [mg/L] | [mg/L]
1 | EP001 | ST | 2014-08-21 | 8:35 | 5 gpm | 5 | 8.5 | 3.4 | 3.62 | 0.5 | 0.005 | 0.3 | 1
2 | 123 2nd AveA | FH | 2014-08-21 | 9:10 | 1000 gpm | 10 | 8.4 | 2.8 | 2.93 | 0.6 | 0.004 | 0.3 | 2
3 | 345 3rd StA | FH | 2014-08-21 | 9:45 | 750 gpm | 10 | 8.5 | 2.4 | 2.52 | 0.7 | 0.005 | 0.3 | 3
4 | 567 4th BlvdB | FV | 2014-08-21 | 10:35 | 50 gpm | 15 | 8.3 | 2.2 | 2.35 | 0.8 | 0.012 | 0.3 | 4
Nitrification
Site ID | Address | Type | Date | Time | Calculated Flow Rate | Minutes Flushed | pH | Total Chlorine* | Mono-chloramine | Free Ammonia | Nitrite | Nitrate
[8 empty] | [mg/L] | [mg/L] | [mg/L] | [mg/L] | [mg/L]
1 | EP001 | ST | 2014-09-20 | 13:00 | 5 gpm | 5 | 8.5 | 3.3 | 3.71 | 0.6 | 0.005 | 0.3 | 1
2 | 123 2nd AveA | FH | 2014-09-20 | 13:30 | 1000 gpm | 30 | 8.4 | 1 | 1.08 | 0.4 | 0.4 | 0.3 | 2
3 | 345 3rd StA | FH | 2014-09-20 | 14:15 | 750 gpm | 90 | 8.5 | 0.4 | 0.39 | 0.3 | 0.368 | 0.5 | 3
4 | 567 4th BlvdB | FV | 2014-09-20 | 14:50 | 50 gpm | 180 | 8.4 | 0.2 | 0.21 | 0.2 | 0.3 | 0.6 | 4
* Post-flush residual
A - Average water age
B - High water age

## DataWorksheet
PWS Name | <PWS Name> | [5 empty] | NAP Baseline/Goal Worksheet
PWS ID | [7 empty] | Responsible Official Name, Signature | [5 empty] | Date
1. NAP Chloramine Effectiveness Suite: Goals and Triggers Data
Input data in yellow areas.
1.a. Entry Point Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each entry point (EP)
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Total Chlorine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Monochloramine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Ammonia
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
1.b. Average Water Age Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each selected site
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Total Chlorine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Monochloramine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Ammonia
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
1.c. High Water Age (Low Residual) Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each selected site
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Total Chlorine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Monochloramine
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Ammonia
Data for setting goals | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
2. NAP Nitrite and Nitrate: Baselines and Triggers Template
2.a. Entry Point Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each entry point (EP)
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Nitrite
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Nitrate
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
2.b. Average Water Age Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each selected site
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Nitrite
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Nitrate
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
2.c. High Water Age (Low Residual) Sample Site Goals | [14 empty] | Determine goals, baselines, triggers for each selected site
SAMPLE SITE No.:______ | [5 empty] | Sample site description (address, tap type, etc):
Collection/analysis procedure:
Nitrite
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Nitrate
Data for determiing baselines, triggers | [13 empty] | Statistics
Date: |  | 2011-01-01 | 2011-01-25 | 2011-02-18 | 2011-03-14 | 2011-04-07 | 2011-05-01 | 2011-05-25 | 2011-06-18 | 2011-07-12 | 2011-08-05 | 2011-08-29 | 2011-09-22 | Average | Std. Dev
Concentration (mg/L): | [13 empty] | #DIV/0! | #DIV/0!
Note on B7: An entry point (EP) is any location where freshly treated water enters the distribution system. You must determine a baseline/goal/trigger for every EP in your system. Insert additional lines if needed.
Note on B56: An entry point (EP) is any location where freshly treated water enters the distribution system. You must determine a baseline/goal/trigger for every EP in your system. Insert additional lines if needed.

## ExampleMAP
Nitrification Action Plan Example
Sample Sites
Site # on Map | Address | Tap Type | Sample Tap Location | Flow Rate (gal) | Flush Time (min)
EP | 281 Pump Station | Hose bibb | Hwy 281 Pump Station, tap on Pump 1 | 5 | 5
1 | 55 E Railway St | Hose bibb | Tap by City Hall parking lot | 2 | 15
2 | 935 Pine St | Hose bibb | Tap in back of house | 2 | 15
3 | 200 W Lamar Blvd | Hose bibb | County Fire Department tap by side door | 10 | 5
4 | 800 W Hwy 190 | Hose bibb | Tap left of front door of High School | 5 | 5
5 | 700 Red River Rd | Hose bibb | Left side of garage | 5 | 5
6 | Hill Top Tank | Hose bibb | Tap on north side of GST | 20 | 5
7 | 10 W Main St | Hose bibb | Bowl-a-Rama tap by back door | 1 | 25
8 | 1164 E CR 400 | Hose bibb | First Memorial Church - tap left of door | 3 | 10
Note on A3: We refer to: u Total chlorine, u Monochloramine, and u Free ammonia as the 'chloramine-effectiveness' suite of chemicals.

## ExampleSampleForm-1
Sample Collection Form |  |  |  | PWS Name | [6 empty] | Initials:
Water Sample ID1 |  |  |  | Flushing Volume2 |  |  |  | Temp/pH |  | Chloramine Effectiveness Group
Site ID | Address | Date | Sample Time | Time Start | Time end | Flow | Volume | Temp | pH | Total Chlorine (as -N) | Mono-chloramine (as -N) | Free Ammonia (as -N)
1. The time and place of sampling create a unique identifier for a sample.
2. To accurately estimate water use, especially at hydrants, an estimated or calculated flow rate is needed

## ExampleSampleForm-2
Sample Collection Form |  |  | PWS Name | [5 empty] | Initials:
Water Sample ID1 |  |  |  | Temp/pH |  | Chloramine Effectiveness Group |  |  | Nitrite/Nitrate
Site ID | Address | Date | Sample Time | Temp | pH | Total Chlorine (as -N) | Mono-chloramine (as -N) | Free Ammonia (as -N) | Nitrate (as -N) | Nitrate (as -N)
1. The time and place of sampling create a unique identifier for a sample.

## ExampleSampleForm-3
PWS Name
Initials:
Sample Collection Form
Water Sample ID1 |  | Flushing Volume2 |  |  | Temp | pH | Total Chlorine (as -N) | Monochloramine & Free Ammonia (as -N) | Nitrate & Nitrate (as -N)
Site ID & Address | Date & Sample Time | Time Start/ Time End | Flow | Volume