# Emergency Preparedness Plan Template

For Affected Utilities in Fort Bend and Harris Counties ONLY

# Assistance

If you need assistance with the EPP template, please fill out the EPP Help Form at www.tceq.texas.gov/goto/epp-help and TCEQ will contact you via email or phone to work with you.

# General Instructions

- On page 1 and 2 complete “General Information” table, circle the option(s) chosen, answer the questions, and sign the certification on page 2.

- Complete Sections I, II, read Section III, in Section IV complete the option(s) chosen that apply to your affected utility, complete Section V as applicable to your affected utility (county judge and sheriff’s office information are required), and complete Section VI Emergency Water Restrictions.

- Attachments A explains the EPP submittal and distribution requirements, and attachments B - D do not have to be filled out but are supplemental information to assist you in the event of an emergency.

# General Information

| Water System Name: |  |
| --- | --- |
| PWS ID No. (if applicable): |  |
| District No. (if applicable): |  |
| County: |  |
| CCN No. (if applicable): |  |
| Owner: |  |
| Prepared by: |  |
| Preparer’s Phone No.: |  |
| Preparer’s Email: |  |
| Preparer’s Mailing Address: |  |
| Preparer Title: |  |
| Preparer’s Organization: |  |
| Plan Implementation Date: The date that options are implemented/installed and functional. |  |

# Option(s) Chosen:

- Refer to Section III-ALTERNATE POWER OPTIONS OVERVIEW.

Circle all Option(s) that will provide emergency operations during extended power outages lasting more than 24 hours for this affected utility.

1     2     3A     3B     4     5     6    7     8

- Short Explanation of Proposed Emergency Preparedness Plan (i.e., Using portable generator to power 2 out of 3 wells):

- Will this plan provide for 35 pounds per square inch (psi) of pressure to all your direct customers during a power outage lasting more than 24 hours caused by a natural disaster?

- Is this a new EPP? (Never submitted before)

# UPDATES TO EMERGENCY PREPAREDNESS PLAN (EPP)

EPPs must be reviewed at least once every 3 years for accuracy. The EPP is updated as changes occur such as dictated by personnel, phone numbers, water plant additions, modifications to chosen option(s), and serving additional water systems. For revised EPP (Use Table Below to document the Purpose and Pages revised) and submit to TCEQ.:

| Last Updated By | Title | Date |
| --- | --- | --- |
| Complete by checking the box for each section updated and by adding information to any subsection that was updated. |  |  |
| EPP SECTIONS | EPP SUBSECTIONS |  |
| Page 1 |  |  |
| - Introduction |  |  |
| - Description of Water System |  |  |
| - Alternate Power Options Overview | No changes |  |
| - Alternate Power Options Details |  |  |
| - Emergency Communication |  |  |
| - Emergency Water Restrictions |  |  |

I certify, under penalty of law, that all the information provided herein is true and accurate to the best of my knowledge. Signature: Title: Date:

# SECTION I – INTRODUCTION

## APPLICABILITY

This emergency preparedness plan template was developed for the operators and administrators of affected utilities to comply with the requirements for “affected utilities” in Texas Water Code, Section 13.1395 as required by Senate Bill 361 (SB 361) and to demonstrate the affected utility’s ability to provide emergency operations during extended power outages lasting more than 24 hours.

An affected utility is a retail public utility, exempt utility, or provider or conveyer of potable or raw water service that furnishes water service to more than one customer, provides overnight accommodations, and is not an affected utility under Texas Water Code, Section 13.1394. An extended power outage means a power outage lasting more than 24 hours.

If you believe that you are NOT an affected utility please email PDWEPP@tceq.texas.gov or call 512-239-1077 to ensure that the requirements do not apply to your water system.

Describe Your Water System. Check all that apply.

Residential		 Commercial	 Industrial		 Wholesale		 Institution

## CONTACT INFORMATION

During any type of emergency, the following person(s) will be responsible for the water system (contact will be attempted in the order indicated):

| Name | Title in the Organization | E-mail | Phone Numbers (include area code) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Office | Cellular | Home | Other |

## Location of Maps

The maps are not required to be submitted to TCEQ for review of the EPP but should be available in case of an emergency to enable staff to locate valves, lines, and meters.

Where are your distribution system(s) map(s) located?

## Diagram of Water System

Submit a diagram of your drinking water system that shows all equipment (source(s), tank(s), pumps), treatment chemicals, and any open or closed interconnects with other water systems.

# Section II – DESCRIPTION OF THE WATER SYSTEM

IMPORTANT: Include only the equipment located at your water system, not the equipment located at another water system unless two or more systems rely on each other during an emergency, and it is documented in a contract or written agreement.

## SOURCE INFORMATION

- Does Your Water System Have Ground Water Well(s)?				        YES  NO  (If NO, go to 1.B)

| TCEQ Source ID | Owner’s Designation | Well Location | Used During an Emergency? | Total Pump Capacity |
| --- | --- | --- | --- | --- |
|  |  |  | YES NO | gpm |
|  |  |  | YES NO | gpm |
|  |  |  | YES NO | gpm |

- Does Your Water System Treat Surface Water or Ground Water Under the Influence of Surface Water Sources(s) (raw water intake pump information)?					YES  NO  (If NO, go to 1.C)

| TCEQ Source ID | Owner’s Designation | Intake Location | Used During an Emergency? | Number of Pumps | Total Pump Capacity at Intake |
| --- | --- | --- | --- | --- | --- |
|  |  |  | YES NO |  | gpm |
|  |  |  | YES NO |  | gpm |
|  |  |  | YES NO |  | gpm |

- Does Your Water System Purchase (or Receive) Water?				YES  NO  (If NO, go to 2.A)

    - Is this affected utility a direct pressure system? (Does the provider’s water flow directly into your distribution system, not into a tank? Direct pressure systems generally have no tanks or pumps.)

YES  NO

    - Does this affected utility re-pressurize the water received from the provider? (Does the water from the provider flow into a tank which is then pumped out into the distribution system by your own pumps?)

YES  NO

| Provider Name | PWS ID | Pressure Plane (if more than 1 plane) | Will You Rely on This Provider for Water During an Emergency? | Will You Rely on This Provider for Pressure at Your Customer’s Connections During an Emergency? | Capacity | Normally Open or Closed Interconnect? |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | YES NO | YES NO | gpm |  |
|  |  |  | YES NO | YES NO | gpm |  |
|  |  |  | YES NO | YES NO | gpm |  |

## TREATMENT INFORMATION

- Does Your Water System Disinfect the Water?						      YES   NO  (If NO, go to 2.B)

| Disinfectant | Location (Plant Name) | Disinfectant Used During an Emergency? | Type of Disinfectant (Liquid/Gas) | Volume Stored (gals or lbs.) | Days of Storage (Emergency Demand) | Electricity Required to Feed Disinfectant? |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | YES NO |  |  |  | YES NO |
|  |  | YES NO |  |  |  | YES NO |
|  |  | YES NO |  |  |  | YES NO |

- Does Your Water System Provide Treatment Other Than Disinfection?      YES   NO  (If NO, go to 2.C)

| Chemical | Location (Plant Name) | Chemical Used During an Emergency? | Type of Chemical (Liquid/Gas) | Volume Stored (gals or lbs.) | Days of Storage (Emergency Demand) | Electricity Required to Feed Chemical |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | YES NO |  |  |  | YES NO |
|  |  | YES NO |  |  |  | YES NO |
|  |  | YES NO |  |  |  | YES NO |

- Does Your Water System Have Service or Transfer Pump(s) In Your Treatment Plant(s)? (Do not include well or intake pumps)                                                                                         YES  NO  (If NO, go to 3.A)

| In-Plant Transfer Pump Name | Location (Plant Name) | Pump Used During an Emergency? | Pump Capacity |
| --- | --- | --- | --- |
|  |  | YES NO | gpm |
|  |  | YES NO | gpm |
|  |  | YES NO | gpm |

## DISTRIBUTION SYSTEM INFORMATION

- Does Your Water System Have Distribution Pumps?					YES  NO  (If NO, go to 3.B)

| Booster/Service Pump Name | Location (include pressure plane) | Pump Used During an Emergency? | Pump Capacity |
| --- | --- | --- | --- |
|  |  | YES NO | gpm |
|  |  | YES NO | gpm |
|  |  | YES NO | gpm |

Does Your Water System Have Any Finished Water Storage/Pressurization Tanks?

YES  NO  (If NO, go to 4.A)

| Tank Type (Elevated (ET), Hydropneumatic (HT or PT), Ground (GST) or Standpipe (ST)) | Location (include pressure plane) | Tank Used During an Emergency? | Tank Capacity |
| --- | --- | --- | --- |
|  |  | YES NO | gal |
|  |  | YES NO | gal |
|  |  | YES NO | gal |

## PRESSURE PLANES

- Does Your Water System Have More Than One Pressure Plane?		YES   NO  (If NO, go to 5)

| Pressure Plane | TCEQ Source ID(s) or Provider PWS ID(s) | Plant Names(s) (If Applicable) | Pump Names(s) (If Applicable) |
| --- | --- | --- | --- |

## SYSTEM DEMAND

Emergency Operation means the demand in MGD from the highest emergency usage day (not normal daily usage) occurring during a natural disaster within the last 3 years, excluding fire events and large water main breaks.

| Demand Information | Normal Operation | Emergency Operation |
| --- | --- | --- |
| Average Daily Demand: | MGD | MGD |
| Maximum Daily Demand: | MGD | MGD |
| System Capacity: | MGD | MGD |

## SYSTEM SIZE

- Does Your Water System Sell/Provide Water to Other Water Systems?	YES  NO  (If NO, go to 6.B)

| Receiver/Buyer Name | PWS ID (if applicable) | Will you provide “water only” to this Receiver During an Emergency? | Will You Provide 35 psi Throughout the Receiver’s Distribution System During an Emergency? | Capacity in GPM sold to Receiver on daily basis | Number of Connections in the Receiver’s Water System | Normally Open or Closed Interconnect? |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | YES NO | YES NO |  |  |  |
|  |  | YES NO | YES NO |  |  |  |
|  |  | YES NO | YES NO |  |  |  |

- Number of Connections and Population in Each Pressure Plane in Your Water System?

(If applicable, include any connections from other water systems you may serve in the table in 6.A)

| Pressure Plane (if applicable) | Number of Connections | Population |
| --- | --- | --- |

## POWER PROVIDER(s)

| Electric Utility or Retail Electrical Provider(s) |  |
| --- | --- |

## ELECTRICAL SCHEMATIC

- Provide an electrical schematic or diagram of your water system’s emergency power facilities and the equipment (treatment(s), supply, pressure maintenance, etc.) that is powered.

## OTHER PERTINENT SYSTEM INFORMATION

Other information about the system that could be useful during an emergency or that will add clarity to your EPP. (This can include plant equipment not used or any other circumstances that would clarify how the affected utility will meet the EPP requirements):

# Section III– Alternate Power Options Overview

The following is a list of options that are available to water systems located in Harris and Fort Bend Counties to demonstrate the ability to provide water to their customers at 35 psi during an extended power outage lasting more than 24 hours. Provide the required information on the applicable pages for each option chosen. Water systems are encouraged to choose as many options as needed to be successful during a power outage lasting more than 24 hours. You must select at least one option and in some cases two.

## OPTION 1: PERMANENTLY INSTALLED AUTOMATIC STARTING AUXILIARY GENERATOR(S)

Fuel requirements: when utilizing a generator option

30 TAC §290.45(h)(6) An affected utility must maintain on-site, or make readily available during emergency operations, an amount of fuel necessary to operate any required emergency power equipment necessary to maintain emergency operations for at least 48 hours.

COMPLETE OPTION 1 – Sections A through C

## OPTION 2: YOUR SYSTEM WILL RELY ON YOUR PROVIDER DURING AN EXTENDED POWER OUTAGE

The type of systems that will utilize this option are a distribution only system which receives water under direct pressure relying on their provider for water and pressure at 35 psi throughout their distribution system. A water system that receives water to a tank and then re-pressurizes the water to maintain 35 psi in their distribution system may also choose this option in addition to a second option that will be used to maintain pressure. Choose if you will rely on a water provider for water and pressure or water only during an extended power outage.

COMPLETE OPTION 2 – Sections A and B

## OPTION 3A: MEMBER OF TXWARN or MUTUAL AID AGREEMENT WITH ANOTHER WATER PROVIDER

Member of TXWARN means you have registered with TXWARN to acquire a generator temporarily or a member of another mutual aid agreement with another water system. A “distribution only” system may only use this option if it needs certified staff for operational purposes or needs equipment to repair their distribution system. A distribution only system will need to choose Option 2 for the purpose of maintaining 35 psi in its distribution system during an extended power outage.

COMPLETE OPTION 3A – Sections A or B, and C

## OPTION 3B: NEGOTIATION OF LEASING AND CONTRACTING AGREEMENT(S)

Your facility has obtained a leasing or contract agreement for a generator, any necessary equipment, and 48 hours of fuel.

COMPLETE OPTION 3B – Sections A through D

## OPTION 4: USE OF PORTABLE GENERATOR(S) CAPABLE OF SERVING MULTIPLE FACILITIES EQUIPPED WITH QUICK-CONNECT SYSTEMS

A portable generator capable of being moved to serve multiple facilities where both the portable generator and facilities are equipped with compatible quick-connect systems. The plan must address whether there is an adequate number of portable generators to operate all necessary water equipment to maintain the required minimum pressure in multiple pressure plans or at multiple systems, if affected by the same natural disaster event.

COMPLETE OPTION 4 – Sections A through D

## OPTION 5: USE OF ON-SITE ELECTRICAL GENERATION OR DISTRIBUTED GENERATION FACILITIES

On-site electrical generation or distributed generation facilities. On-site electrical generation means that each facility generates, or can generate, its own power rather than being powered by a commercial electric power grid. Distributed Generation Facilities are small-scale power producing facilities located near the electrical load, which may feed into a common grid. An example is electricity generated by solar power.

COMPLETE OPTION 5 – Sections A through D

## OPTION 6: HARDENING THE ELECTRIC TRANSMISSION AND DISTRIBUTION SYSTEM SERVING THE WATER SYSTEM

One alternative is to relocate electric transmission lines for the system from overhead to underground and protect them from strong winds. Another alternative is to replace overhead transmission lines, poles and rated appurtenances with ones that can withstand historical hurricane-force wind velocities, and trim or remove any trees or branches next to and above the overhead transmission lines.

COMPLETE OPTION 6 – Sections A and B

## OPTION 7: USE AND MAINTENANCE OF DIRECT ENGINE OR RIGHT-ANGLE DRIVES

Direct engine or right-angle drive.  This option is only available to existing facilities, may require more than one option, and must still provide 35 psi throughout the distribution system.

COMPLETE OPTION 7 – Sections A through C

## OPTION 8: ANY OTHER ALTERNATIVE DETERMINED BY THE COMMISSION TO BE ACCEPTABLE

An affected utility can propose other alternatives of meeting the requirements of TWC 13.1395 if the alternative(s) ensure water will be provided at 35 psi throughout the distribution system during a water outage lasting more than 24 hours.

COMPLETE OPTION 8 – Sections A and B

ALL OPTIONS SELECTED THAT INCLUDE GENERATORS MUST FOLLOW MAINTENANCE SCHEDULE BASED ON SYSTEM SIZE PER 30 TAC RULE §290.46(m)(8).

Emergency generators operated at water systems serving 1,000 connections or greater must be maintained in accordance with Level 2 maintenance requirements contained in the current National Fire Protection Association (NFPA) 110 Standard and manufacturer's recommendation. In addition, the water system must maintain an inventory of operational maintenance items, lubricants, and coolants for critical generator components.

Emergency generators operated at water systems serving fewer than 1,000 connections must be maintained according to manufacturer's specifications, or Level 2 maintenance requirements contained in NFPA 110 Standard. In addition, the public water system must maintain an inventory of operational maintenance items, lubricants, and coolants for critical generator components.

# Section IV– Alternate Power Options Details

## OPTION 1: PERMANENTLY INSTALLED AUXILIARY GENERATOR(S)

- Generator Specifications.

Please list all the generators, all equipment to be powered, and the power needs for each piece of equipment.

| Generator Brand & Model | Max Power (KW)** | Phase | Fuel Type | Automatic Switch Gear Installed? | Facility Staffed 24 hours a day, 7 days a week? | List of all Facilities and Treatment Units That Will Be Powered During an Emergency | Power Requirements for Each Facility and Treatment Unit Powered** |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 2 3 |  | YES NO | YES NO | ### Well pump 1 | kW |
|  |  |  |  |  |  | ### Well pump 2 | kW |
|  |  |  |  |  |  | ### Well pump 3 | kW |
|  |  |  |  |  |  | ### Booster pump 1 | kW |
|  |  |  |  |  |  | ### Booster pump 2 | kW |
|  |  |  |  |  |  | ### Booster pump 3 | kW |
|  |  |  |  |  |  | Disinfection Equipment | kW |
|  |  |  |  |  |  | ### Treatment Equipment | kW |
|  |  |  |  |  |  | ### Compressor(s) | kW |
|  |  |  |  |  |  |  | kW |
|  |  | ### 1 2 3 |  | YES NO | YES NO |  | kW |
|  |  |  |  |  |  |  | kW |
|  |  |  |  |  |  |  | kW |
|  |  |  |  |  |  |  | kW |
|  |  | ### 1 2 3 |  | YES NO | YES NO |  | kW |
|  |  |  |  |  |  |  | kW |
|  |  |  |  |  |  |  | kW |
|  |  |  |  |  |  |  | kW |
| **The generator’s total KWs cannot be less than the KWs listed under the power requirements for each facility and treatment unit that will be provided power. The generator must be able to power the equipment listed by the water system. **An emergency generator used as part of an approved emergency preparedness plan must be inspected, operated, and maintained according to the manufacturer's specifications and the requirements listed in 30 TAC §290.46(m)(8). |  |  |  |  |  |  |  |

- Fuel Location

Physical Location of Fuel Supply (GPS or “911” address):

- Fuel Re-supply. Must have sufficient fuel to provide emergency power for a minimum of 48 hours or more if needed based on past power outages and utility knowledge.

How much fuel is stored on site?

How much fuel does the generator use per hour? (Attachment B may assist in determining that amount)

- Does the water system have access to additives/other methods to prevent fuel from solidifying as per manufacturers’ recommendations (example diesel additives)?

## OPTION 2: YOUR SYSTEM WILL RELY ON YOUR PROVIDER DURING AN EXTENDED POWER OUTAGE

Choose if you will rely on a water provider for water and pressure at 35psi or water only during an extended power outage. You are required to provide written documentation as described below to be able to use this option.

| Provider Name | PWS ID | PRESSURE PLANE | Will you rely on this provider for water to a tank during an emergency? | Will you rely on this provider for pressure at YOUR customer’s connections during an emergency? |
| --- | --- | --- | --- | --- |
|  |  |  | YES NO | YES NO |
|  |  |  | YES NO | YES NO |
|  |  |  | YES NO | YES NO |

- Is your water system solely relying on a provider(s) for emergency operations? (This means, the provider’s water flows directly into your distribution system, and not into a tank, you have no tanks or pumps, and your provider is also providing 35 psi of pressure to your customers.)

NO (Please fill out the pages for the alternative power option(s) that will power the equipment)

YES (If yes, please complete the following.)

- Please provide one or more of the following if relying on provider for water and pressure:

A copy of the contract(s) with your provider(s) that includes language guaranteeing 35 psi throughout your distribution system or specific pressure plane. If your contract(s) with your provider(s) includes emergency capacity sold to your water system, please highlight the section in the contract.

A letter from the provider(s) including language guaranteeing 35 psi throughout your distribution system or specific pressure plane.

Page(s) from the provider’s EPP which includes the connection count for your system (or pressure plane) in the provider’s connection count.

An engineering study (hydraulic analysis) sealed by a Texas Licensed Professional Engineer demonstrating that the provider is capable of providing your entire distribution system with water services at a minimum of 35 psi.

- Does your water system operate any equipment such as booster disinfection or a booster re-pump station that will need power during an emergency?

YES (Please fill out the pages for the alternative power option that will power the equipment)

NO

- Is your water system solely relying on water only from your provider(s) into a tank and your water system will be re-pressurizing the water received from the provider? (This means the water from the provider flows into a tank which is then pumped out into the distribution system by your own pumps. Your water system is not relying on the provider for pressure.)

NO	The tank (GST, ET, STP) will be relying on gravity to provide 35 psi to the water system’s customers.

YES (If yes, you must submit documentation under 2.B.i. listed below and fill out the pages for the alternative power option(s) that will power the re-pressurization equipment.)

- Please provide one or more of the following if relying on provider for water only:

A copy of the contract(s) with your provider(s) that includes language guaranteeing your water system with water. If your contract(s) with your provider(s) includes emergency capacity sold to your water system, please highlight the section in the contract.

A letter from the provider(s) which includes language guaranteeing water to your water system or specific pressure plane.

Page(s) from the provider’s EPP which includes the connection count for your system (or pressure plane) in the provider’s connection count.

- Does your water system operate any equipment such as booster disinfection or a booster re-pump station that will need power during an emergency?

YES (Please fill out the pages for the alternative power option that will power the equipment)

NO

## OPTION 3A: MEMBER OF TXWARN or MUTUAL AID AGREEMENT WITH ANOTHER WATER PROVIDER

Member has identified needed resource(s) to the TXWARN system or to another water system provider as part of a mutual aid agreement. Installation of a quick connect system is required with this option. A “distribution only” system may not use this option to maintain 35psi in distribution. A distribution only system is defined as a system that receives treated water from another entity and does not maintain storage or pressure facilities.

For TXWARN complete A and C.

- Please provide two of the following items:

A copy of the TXWARN membership profile page.

A copy of the mutual aid agreement with TXWARN (Applicable to Investor/Privately Owned Water systems)

A local government entity is covered by the Texas Statewide Mutual Aid System as stated in the Texas Government Code Section 418.111 Subchapter E (Applicable to Cities, Counties, and Districts)

For mutual aid agreement with another water provider(s) complete B and C.

- Please provide ALL of the following items:

Name of water system(s) or group that you have a mutual aid agreement with. _____________

A copy of the mutual aid agreement from each water provider.

Highlight the area in the agreement that lists the resource(s) to be provided by the water system(s).

- Generator specifications

Please list the items hoped to be obtained from TXWARN. List all equipment to be powered, and the power needs for each piece of equipment.

| Generator | Power (KW) | Quick Connect Installed? | Phase | List of all Facilities and Treatment Units That Will Be Powered During an Emergency | Power Requirements of Each Facility and Treatment Unit Powered** |
| --- | --- | --- | --- | --- | --- |
|  |  | YES NO Date to be installed | ### 1 2 3 | ### Well pump 1 | kW |
|  |  |  |  | ### Well pump 2 | kW |
|  |  |  |  | ### Well pump 3 | kW |
|  |  |  |  | ### Booster pump 1 | kW |
|  |  |  |  | ### Booster pump 2 | kW |
|  |  |  |  | ### Booster pump 3 | kW |
|  |  |  |  | Disinfection Equipment | kW |
|  |  |  |  | ### Treatment Equipment | kW |
|  |  |  |  | ### Compressor(s) | kW |
|  |  |  |  |  | kW |
|  |  | YES NO Date to be installed | ### 1 2 3 |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
|  |  |  |  |  | kW |
| **The generator’s total KWs cannot be less than the KWs listed under the power requirements for each facility and treatment unit that will be provided power. The generator must be able to power the equipment listed by the water system. ** An emergency generator used as part of an approved emergency preparedness plan must be inspected, operated, and maintained according to the manufacturer's specifications and the requirements listed in 30 TAC §290.46(m)(8). |  |  |  |  |  |

## OPTION 3B: NEGOTIATION OF LEASING AND CONTRACTING AGREEMENTS

Your water system will obtain an agreement with a generator providing company. Installation of a quick connect system is required with this option. Please note that the agreement must provide for coordination with the Texas Division of Emergency Management.

- Provide a signed copy of the agreement

- Generator Specifications

Please list the generator to be leased, all equipment to be powered, and the power needs for each piece of equipment.

| Generator Brand & Model | Max Power (KW) | Phase | Quick Connect Installed? | Fuel Type | List of all Facilities and Treatment Units That Will Be Powered During an Emergency | Power Requirements for Each Facility and Treatment Unit Powered** |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | ### 1 2 3 | YES NO Date to be installed |  | ### Well pump 1 | kW |
|  |  |  |  |  | ### Well pump 2 | kW |
|  |  |  |  |  | ### Well pump 3 | kW |
|  |  |  |  |  | ### Booster pump 1 | kW |
|  |  |  |  |  | ### Booster pump 2 | kW |
|  |  |  |  |  | ### Booster pump 3 | kW |
|  |  |  |  |  | Disinfection Equipment | kW |
|  |  |  |  |  | ### Treatment Equipment | kW |
|  |  |  |  |  | ### Compressor(s) | kW |
|  |  |  |  |  |  | kW |
|  |  | ### 1 2 3 | YES NO Date to be installed |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  | ### 1 2 3 | YES NO Date to be installed |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
| **The generator’s total KWs cannot be less than the KWs listed under the power requirements for each facility and treatment unit that will be provided power. The generator must be able to power the equipment listed by the water system. **An emergency generator used as part of an approved emergency preparedness plan must be inspected, operated, and maintained according to the manufacturer's specifications and the requirements listed in 30 TAC §290.46(m)(8). |  |  |  |  |  |  |

- Fuel Location

Physical Location of Fuel Supply (GPS or “911” address):

- Fuel Re-supply. Must have sufficient fuel to provide emergency power for a minimum of 48 hours or more if needed based on past power outages and utility knowledge.

How much fuel is stored on site?

How much fuel does the generator use per hour? (Attachment B may assist in determining that amount.)

- Does the water system have access to additives/other methods to prevent fuel from solidifying as per manufacturers’ recommendations (example diesel additives)?

## OPTION 4: USE OF PORTABLE GENERATOR(S) CAPABLE OF SERVING MULTIPLE FACILITIES EQUIPPED WITH QUICK-CONNECT SYSTEM(S)

- Please list the storage location of the portable generator. If sharing the generator, list the name of the water system you are sharing with and their location.

| Generator Brand & Model | Generator Storage Location | Distance (miles) from Your Water System | Other Water Systems Sharing This Generator (PWS Name and ID if applicable) | Distance (miles) Between Your Water System and Those Sharing the Generator |
| --- | --- | --- | --- | --- |

- Generator specifications

Please list all the portable generators, all equipment to be powered, and the power needs for each piece of equipment.

| Generator Brand & Model | Max Power (KW) | Phase | Fuel Type | Quick Connect Installed? | List of all Facilities and Treatment Units That Will Be Powered During an Emergency | Power Requirements for Each Facility and Treatment Unit Powered** |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | ### 1 2 3 |  | YES NO Date to be installed | ### Well pump 1 | kW |
|  |  |  |  |  | ### Well pump 2 | kW |
|  |  |  |  |  | ### Well pump 3 | kW |
|  |  |  |  |  | ### Booster pump 1 | kW |
|  |  |  |  |  | ### Booster pump 2 | kW |
|  |  |  |  |  | ### Booster pump 3 | kW |
|  |  |  |  |  | Disinfection Equipment | kW |
|  |  |  |  |  | ### Treatment Equipment | kW |
|  |  |  |  |  | ### Compressor(s) | kW |
|  |  |  |  |  |  | kW |
|  |  | 1 2 3 |  | YES NO Date to be installed |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
|  |  |  |  |  |  | kW |
| **The generator’s total KWs cannot be less than the KWs listed under the power requirements for each facility and treatment unit that will be provided power. The generator must be able to power the equipment listed by the water system. **An emergency generator used as part of an approved emergency preparedness plan must be inspected, operated, and maintained according to the manufacturer's specifications and the requirements listed in §290.46(m)(8) |  |  |  |  |  |  |

- Fuel Location (if applicable)

Physical Location of Fuel Supply (GPS or “911” address):

- Fuel Re-supply. Must have sufficient fuel to provide emergency power for a minimum of 48 hours or more if needed based on past power outages and utility knowledge.

How much fuel is stored on site?

How much fuel does the generator use per hour? (Attachment B may assist in determining that amount.)

Does the water system have access to additives/other methods to prevent fuel from solidifying as per manufactures’ recommendations (example diesel additives)?

## OPTION 5: USE OF ON-SITE ELECTRICAL GENERATION OR DISTRIBUTED GENERATION FACILITIES

Onsite Electrical Generation means that each facility generates its own power rather than being powered by a commercial electric power grid. Distributed Generation Facilities are small-scale power producing facilities located near the electrical load which may feed into a common grid.

- On-Site Electrical Generation or Distributed Generation Specifications

Describe On-Site Electrical Generation or Distributed Generation Facility:

- On-site Electrical Generation or Distributed Generation Specifications

Please list all facilities, list all equipment to be powered and the power needs for each piece of equipment.

| Type of On-site Electrical Generation Facilities. | Max Power (KW) | Fuel Type (if applicable) | List of all Facilities and Treatment Units That Will Be Powered During an Emergency | Power Requirements of Each Facility and Treatment Unit Powered** |
| --- | --- | --- | --- | --- |
|  |  |  | ### Well pump 1 | kW |
|  |  |  | ### Well pump 2 | kW |
|  |  |  | ### Well pump 3 | kW |
|  |  |  | ### Booster pump 1 | kW |
|  |  |  | ### Booster pump 2 | kW |
|  |  |  | ### Booster pump 3 | kW |
|  |  |  | Disinfection Equipment | kW |
|  |  |  | ### Treatment Equipment | kW |
|  |  |  | ### Compressor(s) | kW |
|  |  |  |  | kW |
|  |  |  |  | kW |
|  |  |  |  | kW |
|  |  |  |  | kW |
|  |  |  |  | kW |
|  |  |  |  | kW |
| **If using a manually starting generator the total KWs cannot be less than the KWs listed under the power requirements for each facility and treatment unit that will be provided power. The generator must be able to power the equipment listed by the water system. **An emergency generator used as part of an approved emergency preparedness plan must be inspected, operated, and maintained according to the manufacturer's specifications and the requirements listed in §290.46(m)(8) |  |  |  |  |

- Fuel Location

Physical Location of Fuel Supply (GPS or “911” address):

- Fuel Re-supply. Must have sufficient fuel to provide emergency power for a minimum of 48 hours or more if needed based on past power outages and utility knowledge.

How much fuel is stored on site?

How much fuel does the generator use per hour? (Attachment B may assist in determining that amount)

Does the water system have access to additives/other methods to prevent fuel from solidifying as per manufactures’ recommendations (example diesel additives)?

## OPTION 6:	HARDENING THE ELECTRIC TRANSMISSION AND DISTRIBUTION SYSTEM SERVING THE WATER SYSTEM

One alternative is to relocate electric transmission lines for the system from overhead to underground and protect them from flooding. Another alternative is to replace overhead transmission lines, poles and rated appurtenances with ones that can withstand historical hurricane-force wind velocities, and trim or remove any trees or branches next to and above the overhead transmission lines.

- Hardening Description

Describe the hardening activities:

- Diagram

Include a diagram showing the electrical system, including the power transmission system (from the power generation facility to the customer’s power meter) and distribution system (the water system’s electrical wiring after the customer’s power meter) feeding each water facility and the preventive measures taken for each.

## OPTION 7: USE AND MAINTENANCE OF DIRECT ENGINE OR RIGHT- ANGLE DRIVES (EXISTING FACILITIES ONLY) This option is only available to existing facilities and may require more than one option. A second option may be required if a right angle drive is located only on a well, to explain how will treated water be sent to the distribution system, or if located only on a booster pump, to explain how is treated water entering a storage tank, and the water system must still provide 35 psi throughout the distribution system.

- Direct Engine or Right-Angle Drive Specification

- Please list all the drives, all equipment to be powered, and the power needs for each piece of equipment.

| Brand or Model | Max Power (HP, kW) | RPM | Fuel Type | List of all Facilities and Treatment Units Powered | Power Requirements of Each Facility and Treatment Unit Powered (circle appropriate unit) |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | ### Well pump 1 | kW or HP |
|  |  |  |  | ### Well pump 2 | kW or HP |
|  |  |  |  | ### Well pump 3 | kW or HP |
|  |  |  |  | ### Booster pump 1 | kW or HP |
|  |  |  |  | ### Booster pump 2 | kW or HP |
|  |  |  |  | ### Booster pump 3 | kW or HP |
|  |  |  |  | Disinfection Equipment | kW or HP |
|  |  |  |  | ### Treatment Equipment | kW or HP |
|  |  |  |  | ### Compressor(s) | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |
|  |  |  |  |  | kW or HP |

- Fuel Location (if applicable)

Physical Location of Fuel Supply (GPS or “911” address):

- Fuel Re-supply. Must have sufficient fuel to provide emergency power for a minimum of 48 hours or more if needed based on past power outages and utility knowledge.

How much fuel is stored on site?

How much fuel does the generator use per hour? (Attachment B may assist in determining that amount.)

Does the water system have access to additives/other methods to prevent fuel from solidifying as per manufactures’ recommendations (example diesel additives)?

## OPTION 8: ANY OTHER ALTERNATIVE DETERMINED BY THE COMMISSION TO BE ACCEPTABLE

An affected utility can propose other alternatives of meeting the requirements of TWC 13.1395 if the alternative(s) ensure water will be provided at 35 psi throughout the distribution system during a water outage lasting more than 24 hours.

- The following methods would NOT be acceptable options

- Evacuation

The EPP must show how you will provide water during an extended power outage caused by a natural disaster, not during the disaster when it is unsafe. The rule specifically states the water is to be provided after it is safe and practicable. The people who are evacuated may return when it is safe to do so after the disaster has passed, but before power is returned to your water system. In the case of the most recent winter storm, power was not restored for several days. You must be able to provide water after the disaster, but before normal power is restored.

- Providing bottled water

The EPP must show how you will provide water at 35 psi at each of your customer’s connections.

- Relying on your provider without the documentation that states the provider will provide your system with 35 psi throughout your distribution system.

- B.	Alternative Description

Describe the alternative and how it will provide 35 psi throughout your distribution system:

# Section V – Emergency Communications

Emergency Communications are an essential part of an emergency response event. Knowing who to notify before an emergency event occurs is the best way to ensure that you, your system, and your customers receive needed emergency assistance. Many numbers have been provided to assist you with completing this portion of the plan. Please feel free to make copies of the pages in Section IV to post at your facility and/or to train your employees.

If the Organization is not applicable to your utility, please enter N/A. You are required to provide phone numbers for your County Judge and County Sheriff’s Office.

If you are a member of another mutual aid organization other than TXWARN please include them on this list.

- Emergency Contacts

| Organization | Phone Numbers (including area code) |  | E-Mail or Website |
| --- | --- | --- | --- |
|  | Day | Evening |  |
| Fire Department | 911 | 911 |  |
| Police Department | 911 | 911 |  |
| Emergency Medical Service | 911 | 911 |  |
| TCEQ Water Homeland Security | 888/777-3186 | 888/777-3186 |  |
| Texas PUC | 512/936-7405 |  | http://www.puc.texas.gov/industry/water/utilities/fmt.aspx Email: water@puc.texas.gov |
| National Response Center | 800/424-8802 | 800/424-8802 | http://nrc.uscg.mil/Default.aspx |
| State Spill Hotline | 800/832-8224 | 800/832-8224 | https://www.tceq.texas.gov/response/spills |
| Poison Control | 800/222-1222 | 800/222-1222 | http://poisoncontrol.org/home/ |
| CHLOREP (Chlorine Emergency Plan) | 800/424-9300 | 800/424-9300 | https://www.chlorineinstitute.org/emergency-preparedness/chlorep/ |
| TCEQ Regional Office 12 | 24-hour cell phone 512/965-2717 |  | Website: https://www.tceq.texas.gov/agency/directory/region/reglist.html |
| County Judge |  |  | Email: Website: |
| County Office of Emergency Management |  |  | Email: Website: |
| County Sheriff’s Office |  |  | Email: Website: |
| County Public Health & Environmental Services |  |  | Email: Website: |
| City Mayor’s Office |  |  | Email: Website: |
| Local Public Health & Environmental Services |  |  | Email: Website: |
| Local Office of Emergency Management |  |  | Email: Website: |
| TX Division of Emergency Management (TDEM) | Provides list of State and District Coordinators which assist local officials with state assistance requests. Requests must start at local level first. |  | https://tdem.texas.gov/regions |
| TXWARN | 866/9-TXWARN (866/989-9276) |  | Email: info@txwarn.org https://www.txwarn.org |
| Other Mutual Aid Provider |  |  | Email: Website: |

- Local Contact Notification List

Identify those entities that should be notified in the event of an extended power outage requiring emergency operations. These are people who you provide water to that you may need to contact during an emergency.

| Organization | Contact Name | Title | Phone Numbers (including area code) |  |  | E-Mail |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Day | Evening | Cellular/Pager |  |
| Other Local Government Officials |  |  |  |  |  |  |
| Hospitals served by the Affected Utility |  |  |  |  |  |  |
| Nursing Homes served by the Affected Utility |  |  |  |  |  |  |
| Pharmacies |  |  |  |  |  |  |
| Priority Water Users (Those that are critically dependent upon water including schools, dialysis centers, institutions, individuals with special needs, businesses, and other interconnected water systems, etc.) |  |  |  |  |  |  |
| Others |  |  |  |  |  |  |

- Chemical Supplier Information

Identify your Chemical Suppliers. You may need to contact them for more chemicals during an emergency

| Chemical | Supplier | Contact Name | Phone Number Day | Phone Number Evening | Cell Phone | E-Mail |
| --- | --- | --- | --- | --- | --- | --- |

- Certified Laboratory Information

Identify your laboratory and a backup laboratory. You may need a backup laboratory if your primary lab is nonfunctional.

|  |  |  | Phone Numbers (including area code) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Organization | Contact Name | Title | Day | Evening | Cellular/Pager | E-Mail |

- Fuel Supplier Contact Information (if applicable)

Identify your Fuel Suppliers. You may need to contact them for fuel during an emergency

| Fuel Type | Supplier | Contact Name | Phone Number Day | Phone Number Evening | Cell Phone | E-Mail |
| --- | --- | --- | --- | --- | --- | --- |

- Utilities Contact Information

Identify your Utilities Contacts. You may need to contact them during an emergency and use N/A if a listed organization does not apply to your water system.

|  |  |  |  | Phone Numbers (including area code) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Organization | N/A | Contact Name | Title | Day | Evening | Cellular/Pager | E-Mail |
| Electric Utility Company |  |  |  |  |  |  |  |
| Gas Utility Company |  |  |  |  |  |  |  |
| Sewer Utility Company |  |  |  |  |  |  |  |
| Telephone Utility Company |  |  |  |  |  |  |  |
| Wholesale Water Provider |  |  |  |  |  |  |  |
| Wholesale Water Provider |  |  |  |  |  |  |  |
| Other |  |  |  |  |  |  |  |

- Bulk Water Suppliers

Identify any bulk or bottled water suppliers that you might utilize in an emergency.

|  |  |  | Phone Numbers (including area code) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Organization | Contact Name | Title | Day | Evening | Cellular/Pager | E-Mail |
| Bulk Water Haulers |  |  |  |  |  |  |
| Bottled Water Sources |  |  |  |  |  |  |

- Media Notification List

Identify the media organizations that you might need to contact to provide information to your customers. Also identify who your media spokesperson is. If you have a different method to communicate to your customers, please list under Other.

| Organization | Contact Name | Title | Day | Evening | Cellular/Pager | E-Mail |
| --- | --- | --- | --- | --- | --- | --- |
| Designated Water System Spokesperson |  |  |  |  |  |  |
| Newspaper - Local |  |  |  |  |  |  |
| Newspaper – Regional State |  |  |  |  |  |  |
| Radio |  |  |  |  |  |  |
| Television |  |  |  |  |  |  |
| Other |  |  |  |  |  |  |

# Section VI - Emergency Water Use Restrictions

EXPLANATION AND AUTHORITY

During periods of drought, a major leak, a system failure, or excessive consumption beyond the capacity of the system, etc., the       (e.g. PWS name, owner name, owner representative, Operator, etc.) has the capability to conserve and restrict water use based upon the local water system regulations found in       (Drought contingency plan, rental agreement, city ordinance, etc.). During times of drought or other problems that limit the availability of water, public notice of water use restrictions will be issued by:       (e.g. PWS name, owner name, owner representative, Operator, etc.).

            - WATER RESTRICTION STAGES		N/A

The following are levels or stages of restrictions that will be applied, the conditions that generally will trigger them and the types of restrictions that will be applied. The conditions that trigger various restriction stages could be based upon critical source water levels and other conditions such as imminent loss of water or pressure.

| Restriction Stage | Stage Trigger(s) | Restrictions |
| --- | --- | --- |
| I |  |  |
| II |  |  |
| III |  |  |

# ATTACHMENT A – SUBMITTING COMPLETED EPP

Upon completing your EPP please email or mail (not both) the completed form and additional documentation needed to the Texas Commission on Environmental Quality for review and approval to:

Choose One

PDWEPP@tceq.texas.gov

OR

Water Supply Division, Emergency Preparedness and Response Section, MC-151

P.O. Box 13087

Austin, TX 78711-3087

## Assistance

If you need assistance with completing the EPP template, please fill out the EPP Help Form at www.tceq.texas.gov/goto/epp-help and TCEQ will contact you via email or phone to provide assistance.

## Approved Plan Distribution

Complete this section after the approval letter is received from TCEQ. Please maintain appropriate documentation of compliance with plan distribution requirements. In addition, a copy of the approved plan must be maintained by the “affected utility”, so that it can be easily accessed in the event of an emergency. All employees must receive annual training on implementation of the plan.

Copies of the approved Emergency Preparedness Plan and the TCEQ Approval Letter must be distributed to the following entities:

| Distributed To | Method of Distribution | Date |
| --- | --- | --- |
| County Judge |  |  |
| County Office of Emergency Management |  |  |
| Public Utility Commission Filing | Use the weblinks provided: For Confidential filing procedures for the PUC use Docket No. 52272 - http://puc.texas.gov/industry/filings/Confidential.aspx For PUC Procedural Rules for Filing of Pleadings, Documents, and Other Materials - http://puc.texas.gov/agency/rulesnlaws/procrules/pr-e/22.71/22.71.pdf Address: Public Utility Commission of Texas Central Records 1701 N Congress PO Box 13326 Austin, Texas 78711-3326 For additional questions contact the PUC Central Records office at (512)936-7180. |  |
| Texas Division of Emergency Management (TDEM) | Submit to TDEM via email at: soc@tdem.texas.gov Address: Texas Division of Emergency Management Attn: Tech Hazards 2883 Highway 71 E PO Box 285 Del Valle, Texas 78617 For additional questions contact the TDEM (512)424-2208 |  |

# ATTACHMENT B – Generator Information

If you plan on utilizing options 1, 4, 5, or 7 you will need to estimate the gallons per hour of fuel that will be used by the generator. This is essential in determining the volume of fuel required to maintain emergency operations. Below is a chart from the FEMA Resource Typing Manual which may be of assistance in determining fuel needs and generator types. Supplemental information only.

# ATTACHMENT C – RECOVERY CHECKLIST – Supplemental Information Only

Returning to normal operations is vital to rapid restoration of clean, safe water to the community and is essential to the assessment and recovery process. The following is a checklist of actions to be taken during the recovery period. Also included is a preliminary damage assessment that can be used to assist in the recovery process.

## Assessment and Recovery Period Checklist

Perform in-depth damage assessment of system to determine long-term effects of damaged areas (use assessment form below).

Notify TCEQ of system operational status and situation.

Will there be a need to use mutual aid agreements and/or implement standby contracts or other emergency agreements for equipment and operations?

Prepare written documentation of emergency work performed for possible compensation by emergency agencies. Make sure that crews make a record of work effort, written logs (see Work Order Log) and take pictures. This will all be helpful in recovery of funds.

Notify appropriate insurance carriers. Provide written and photo documentation of damage.

Assist in the survey of emergency repairs and scheduling of permanent repairs.

Service the emergency equipment, when able (oil changes, lubrication, etc.).

Keep the public informed throughout the extent of the emergency.

## Preliminary Damage Assessment

Following the Damage Assessment, you should notify TCEQ of your operational status.

- General Overview:

Determine need to repair, replace, or abandon facilities

Estimate cost to repair damage

Evacuate buildings in danger of collapse

- Treatment Plants:

Check if power is available and condition of mechanical and electrical equipment

Check for chemical spills or releases

- Confirm that field crew does the following:

Check for structural damage

Closes and tags damaged facilities and equipment

- Reservoirs:

Check for leaks and seepage

Check for Cracks

Check for Broken inlet/outlet pipes, underdrains

Check for Landslides or Embankment slump

Check for Buckling

Distribution System:

Check for leaks

Check for breaks

Pressure loss in lines

Cross-connections

Check mechanical couplings

Lower water levels to reduce possibility of structural damage

- Wells:

Check for physical damage to facilities

Test for contamination

Name, address, phone # for private lab

Check for pump or motor failure

Check power source

- Tanks:

Check for evidence of failure of subbase

# ATTACHMENT D – State Assistance Request (Supplemental Information Only):

If an affected utility is interested only in mutual aid assistance, register with TXWARN at https://www.txwarn.org/; this is a free service.

When requesting state assistance, the request(s) must start at the local level with the County Judge or the County Emergency Manager. The request must go to the State of Texas Assistance Request using the steps outlined in the STAR Process.